## Sheet1
Concern Worldwide, Bangladesh
Tender Reference: BGD/DHK/Solar/TENDER/2023/004 |  |  | Annex : 5
Financial Offer Form
Tender for: Solar installation project
Name of Project: Solar installation project
Company name:
Items | Description | Unit Number | Unit Price | Total (Taka)
Solar PV panels | At minimum 18% solar panel, Tier-1 Branded (Total 28kWp) |  |  | 0
Grid tied Inverter | String inverter, 20 kW, 3-phase, 50 Hz, Compatible with SREDA standards |  |  | 0
Hybrid Inverter (For backup system) | Grid Tied hybrid inverter,3.5x3 = 10.5 kW, 50 Hz |  |  | 0
Battery (For backup system) | 12 volt 200amp battery, total 12 individual battery. (4 individual battery will be combined to make a 48 volt unit, total of 3 unit. Each 48 volt unit will be connected to separate hybrid inverter) |  |  | 0
Mounting structure | Panels needs to be mounted at a 23 degree angle and the sturcture needs to strong enough to tackle cyclones and any other concerning natual disater (A hypothetical design is given in Annex 4) |  |  | 0
Cables including cable tray and combiner box | Wire needs to be capable of carrying high amps and fire resistant. The combiner box needs to be IP65 rated. |  |  | 0
Status monitoring equipment | The monitoring tools needs to be connected to a computer or a software where the relevant information will be stored. |  |  | 0
Lightning Protection system (LPS) | Ensure proper LPS connections on both the DC and AC sides with a resistance of less than 5 ohms. |  |  | 0
AC and DC components | The system should include IP 65 protected AC and DC distribution components. |  |  | 0
Fuel check controller | A controller which will combine the solar and generator electricity supply. This will maintain the balance in power supply from both generator and solar system when national grid is offline. |  |  | 0
Equipment for maintenance |  |  |  | 0
Net Energy Meter | Must be from SRDEA aprroved list |  |  | 0
Getting regulatory permissions and others |  |  |  | 0
|  |  | Total | 0
Signature
Name and designation
Date