Technical Specification Form

Tender for:  Solar Panel installation

Name of Project: Solar Panel installation

Tender Reference: BGD/DHK/Solar/TENDER/2023/004

Annex-4

Please review this Table and other specifications before answering the following questions

| Equipment | Specifications | Additional Technical Evaluation Indicators |
| --- | --- | --- |
| Area | 2454 Sqft or 227.98 Square M |  |
| System Capacity and PV Solar Panels | 18kWp (kW peak) system along with 10kWp for backup system. All total a 28 kWp system. Minimum 18% efficient (monocrystalline), tier-1 branded | Efficiency (%), Coefficient of temperature (%/degree C), Power rating / sq metre |
| Grid Tied Inverter | String inverter, 20 kW, 3-phase, 50 Hz, Compatible with SREDA standards | Inverter efficiency (%), Operating temperature parameters |
| Hybrid Inverter | Grid Tied hybrid inverter,3.5x3 = 10.5 kW, 3-phase, 50 Hz | Inverter efficiency (%), Operating temperature parameters |
| Battery Bank | Total capacity 1,600 Ah, 48 Volt unit | AGM Lead Acid, Operating temperature parameters, discharge capacity |
| Mounting Structure | Panels mounted on office roof at an angle of 23 degrees to the horizontal. | Allowing access walkways for maintenance, inspections, etc. |
| Cables, Cable Tray, Combiner Box | Wire needs to be capable of carrying high amps and fire resistant. The combiner box needs to be IP65 rated. | For DC and AC there will be different requirement of wire rating and category but both need to have 25% extra load capacity. |
| Fuel check controller / sma fuel save Controller | A controller which will combine the solar and generator electricity supply. This will maintain the balance in power supply from both generator and solar system when national grid is offline. | Supplier will ensure required controller which support both solar panel and diesel fuel generator |
| Status Monitoring Tools | The monitoring tools needs to be connected to a computer or a software where the relevant information will be stored. | Status monitoring tools is to be used for tracking the solar production over time. Also, monitoring equipment will be used for seeing if any part of the solar panel is malfunctioning. |
| Lightning Protection System | With resistance < 5 ohms |  |
| AC/DC Components | IP65 rated and fire resistant |  |
| Equipment for Maintenance | No specification |  |
| Net Energy Meter | SREDA and BSTI approved |  |
| Construction works |  | Access walkways, protective fencing |
| Getting regulatory permissions and others |  |  |

Other specifications are-

- Grid tied Inverter- Inverter must be from following list in the given webpage link- http://sreda.gov.bd/site/page/ef10447e-509a-4e7d-94ad-df2eaf5c27ec

- Net Energy meter- Product must be from the list of product approved by SREDA. Net meter list-https://solar.sreda.gov.bd/nem/gridtiedinverter.php

Figure: A hypothetical design structure for the solar panels