## Summary_Overall
PROJECT: | Planning & Design of Community Piped Water Supply Systems for Rohingya Camps, Cox's Bazar, UNICEF
CLIENT: | UNICEF
SUBJECT: | Cost Estimation
DATE:
Overall Cost Summary (Camp 15 Block D&E)
Item No | Description of Items | Amount in BDT
Part C | Electro-mechanical Works
Part C1 | Mechanical Works (Submersible and Chlorine Pump with Accessories) | 0
Part C2 | Solar System Works (Main Energy Source) with Necessary Foundation Works | 0
Part C3 | Electrical Works | 0
Sub-Total of Part C |  | 0
Grand-Total |  | 0

## Part_B2D (hidden)
Land Development, Landscaping & Plantation
Item SL. | PWD SOR 2022 | Description of Items | Unit | Quantity | Unit Rate (BDT) | Amount (BDT)
Part-4: Land Development, Landscaping & Plantation
1.01 | 25.1 | Labour charge for scraping lawn surface up to 38 mm depth by spade, picking up all sorts of brick bats, rubbish by suitable tools, removing the same by head load or by any other means and stacking the same to a safe distance beyond 300 m including supply of tools and plants etc. all complete and accepted by the Engineer-in-charge. | sqm | 60.5 | 20 | 1210
1.02 | 25.2 | Preparation of ground to make ready for plantation by spading the ground to a depth of 150 mm to 230 mm beyond 38 mm deep scrapped ground by spade, breaking earth clods to powder by hammers, picking up all sorts of rubbish, unwanted grasses by suitable tools, carrying and spreading the surplus earth into low lying area including supply of tools and plants etc. all complete and accepted by the Engineer-in-charge. | sqm | 60.5 | 30 | 1815
1.03 | 25.3 | Leveling and dressing of lawn area to proper slope and grade by spading the same including supplying tools and plants etc. all complete and accepted by the Engineer-in-charge. | sqm | 60.5 | 10 | 605
1.04 | 25.4 | Supply of best and approved quality alluvial loamy silty soil including loading, unloading at both ends, properly stacking at site including supply of tools and plants etc. all complete and accepted by the Engineer-in-charge. | cum | 18.15 | 1100 | 19965
1.05 | 25.5 | Supply well decomposed cow dung carried by trucks or any other means including loading, unloading at both ends, stacking the same at site including supply of tools and plants etc. all complete and accepted by the Engineer-in-charge | cum | 3.025 | 2042 | 6177.05
1.06 | 25.6 | Labour charge for spreading the alluvial loamy silty soil from the stacks at site on the lawn surface, leveling, dressing the same including supply all necessary tools and plants etc. all complete and accepted by the Engineer-in-charge. | cum | 18.15 | 230 | 4174.5
1.07 | Analysis | Planting different types of tree plants one year old 1m high with vigourous canopy& stright trunk in/c carriage (Amloki ,hotoki, bash , panchutia., pata, bohera, ashothoBot, tulsi, ulot kombal, bell,, mango, jam , sofeda, gab, kodbell, chalta, boroi, lotkol, jamrul etc ,nagachua, kat golap, bottle brush. krishnochura, kamini, jolpi, nim ) | each | 20 | 220 | 4400
[5 empty] | Total | 38346.55

## Part_C1
Part C1: Mechanical Works (Submersible Pump with Accessories)
Sl | Description of Works | Unit | Qty. | Unit Price (BDT) | Total Amount (BDT)
1 | Providing of & testing (BUET / MIST or any other public organization) following capacity multistage Bore-well Submersible water Pump Motor set manufactured according to relevant BDS standard and ISO 9906:2012, Grade 3B / DIN / NEMA / IEC / BS / VDE / JIS & ISO 9001:2015 standard. CE certified / UL listed comprising of 2900 RPM, single/ three phase submersible rewindable type (oil / water cooled ) motor having insulation: Class F & Protection: IP68 (minimum), suitable for operation at 230 /400 V ± 5% , 50 Hz AC supply, in built non-return valve with at least 3Cx16 sq.mm submersible marine cable with required length and it shall be in a single length) including dry run with overflow protection sensor system with signal cable etc. complete in all respect manufactured by company having minimum 30 years of manufacturing experience. Country of Manufacture: EU Countries/USA/Japan/UK, in their own industry as per sample accepted / approved by the Engineer-in-charge. (Brand: Wilo-Germany, Saer-Italy, KSB-Germany, Foras-Italy or Equivalent) | Set | 1 |  | 0
| Specification of Pump Motor Set : |  |  |  | 0
| Pump Type: Mixed flow, vertical installation, borehole type, multi stage submersible water pump. |  |  |  | 0
| Discharge: 5-50(25) m3/h, Total Dynamic Head: 90-30(57) m, Motor HP: 10 The head-Discharge point must be inside of +/- 10% of midpoint of the pump performance curve. |  |  |  | 0
| Motor Type: Heavy duty, water Lubricated, water filled, squirrel cage induction motor, re-windable and overhung type winding suitable for continuous operation. |  |  |  | 0
| Combined efficiency: Maximum combined efficiency to be quoted by the supplier and substantiated by performance curve and shall not be less than 60% |  |  |  | 0
| Material Specification of Pump Impeller, Shaft, diffuser, casing & Bowl: Stainless steel-304/316 |  |  |  | 0
| The actual design discharge 25 m3/hr. The actual head is to be informed after the step drawdown test of PTW at the implementation stage. |  |  |  | 0
2 | Providing of 75 mm (3") dia 3 meter (10'-0) long column pipe to be connected with submersible Pump Motor set made of GI column pipe "Special" grade (minimum thickness 4 mm ) with all standard accessories including special flange at both ends including anticorrosive painting etc. as per sample accepted / approved by the Engineer-in-charge. | each | 16 |  | 0
3 | Supply of 4mm thick 75 mm (3") minimum 1'-0" long MS Nipple Pipe (one end outer threaded and other end flanged) for interconnection of submersible pump delivery and with the first set of flanged riser pipe all complete | Set | 1 |  | 0
4 | Installation, testing and commissioning of the deep well submersible pump-motor set by lowering down and connecting pump bowl assembly and column pipes with marine cable with the help of chain pulley after checking and testing the Pump Motor set including filling distilled water supplying and fixing a long bend, 6.35 mm thick 450mm dia. MS sheet tube-well cover required heavy duty holding clamp with nuts, bolts, and making all electrical and pipe connection complete as per direction of the Engineer-in-charge. | Set | 1 |  | 0
5 | Supplying, installing, fixing and jointing the following new pipes, fittings and specials (painted with enamel paints over a coat of anticorrosive primer) in correct position and alignment including supply of 2 nos 3mm thick rubber gaskets and hit dip GI Nut-Bolts for each flanged joints etc. all complete as per drawing and design and the direction of the Engineer-in-Charge. |  |  |  | 0
5.1 | 75mm dia. 4mm thick MS Pipe | m | 10 |  | 0
5.2 | 75mm dia. 4mm thick 90o MS flanged bend | each | 2 |  | 0
5.3 | 75mm dia. 4mm thick 45o MS flanged bend | each | 2 |  | 0
5.4 | 100 x 100 x 75 mm MS Tee (flanged) | each | 0 |  | 0
5.5 | 75mm dia. CI flanged adapter with rubber ring | each | 1 |  | 0
5.6 | 100 mm dia. Sluice Valve | each | 0 |  | 0
5.7 | 75 mm dia. Sluice Valve | each | 1 |  | 0
5.8 | 75 mm dia. Non-return Valve | each | 1 |  | 0
5.9 | 20 mm dia. Automatic Air Release Valve | each | 1 |  | 0
5.10 | 0 to +6 bar Pressure Gauge | each | 1 |  | 0
5.11 | 20mm thick 150mm outer dia loose flange for 75mm dia. Pipe | each | 15 |  | 0
5.12 | 20mm thick 220mm outer dia loose flange for 100mm dia. Pipe | each | 10 |  | 0
5.13 | 75 mm dia. Ms Washout Pipe | m | 5 |  | 0
6 | Supplying, Installing, fixing and jointing the 75mm dia. sensor type bulk water meter to newly Installed PTW in correct position and alignment including supply of necessary fittings etc. all complete as per drawing specification and direction of Engineer-in-Charge. | each | 1 |  | 0
7 | GV RCC Post: Manufacturing, supplying & fixing in position RCC (1:2:4) Pillars of size 150mm x 150mm x 750mm, with 400mm x 400mm x 100mm base having 3 nos. 10mm dia MS bar each way at base, 4 nos. 10mm dia vertical bar and 8 nos. 6mm dia tie, including cost of form works, concreting, reinforcement, plastering at top, inscribing on exposed surface, finishing surface, curing, earth cutting, embedding 450mm below GL., backfilling, ramming etc. complete as per direction of E-I-C. | each | 2 |  | 0
8 | Supply and install chlorine dosing pump with polyethylene 50 liter tank and accessories and according to technical specifications complete as per direction of E-I-C. | each | 1 |  | 0
Total Amount, BDT |  |  |  |  | 0

## Part_C2
Part C2: Solar System Works
Sl | Description of Works | Unit | Qty. | Unit Price (BDT) | Total Amount (BDT)
1 | Solar Module: Supplying, installation, testing & commissioning of 36 x 550Wp(2 strings, each of 18 modules) for on grid & 1x250Wp for off grid solar module with required quantities of mono / poly crystalline silicon solar PV modules as per following standards, specifications and certification. The system will be able to produce power for supplying to grid with required compatible solar cables (DC cables) and all necessary accessories to complete the installation providing one-year free operation & maintenance of the system. Solar system shall have to comply following specification: | Wp | 20050 |  | 0
| I. Parameters for PV Module should be at Standard Test Condition of solar irradiance of 1000 W/m2, Cell Temperature of 25 degree Celsius and AM of 1.5g. II. Solar PV module shall be inconformity with the requirement of BDS IEC 61215, IEC 61730 (latest edition) along with VDE/NEMA/JIS/BS standards. Certificate issued by the internationally recognized authority such as CE / TUV /DNV or equivalent certifying body shall have to be submitted by the bidder for the above mentioned international standard. Manufacturing facility should be ISO9001, ISO14001 quality management system certified. |  |  |  | 0
| III. Solar modules shall be installed pointing to the right direction to capture most of the solar energy to transform it into electricity with the facility to be adjusted from the horizontal to 12 degree in summer and to 35 degree in winter to get the maximum efficiency and must face the true south in our country. For fixed panel mounting system, the panels must be tilted (22.5 ± 1) degree with horizontal and must face the true south in BANGLADESH. IV. The average efficiency of PV module should be minimum 20%. V. The complete PV module shall be diode protected at junction box to protect reverse current. VI. Operating temperature range should be -40 to 85 Degree Celsius. |  |  |  | 0
| VII. Power de-rating allowed should be not more than (-0.41%)/Degree Celsius VIII. Panels should be constructed with anti-reflective glass,anti PID, IX. Modules fitted with anodized aluminum frames or, if without frame, two-glass modules. |  |  |  | 0
| X. Resistance to a maximum pressure load of 5400 Pa and vacuum of 2400 Pa (according to BDS IEC 61215) XI. Each module will be provided with a clearly visible identifier bearing the name, the model of the module and a visual identification or a serial number which allows the traceability of the date of manufacture in accordance with standard NF EN 50380 XII. Each combiner box of PV module shall be diode protected to ensure any back flow current to the PV array and may have fuse of adequate ratings in DC positive line of the PV array and wire terminals. The main combiner box shall have lightning surge protective device of as per nominal voltage of the combiner box both in positive and negative line in order to ensure the bypass diode always function even in thunder storm. The fuse, if exists, shall also have disconnection switch .The box shall be completely water proof according to IP 68. XIII. Product warranty against manufacturing defects : minimum 12 years and their replacement during this period XIV. Performance warranty: linear degradation, minimum 98% at 1 year, then linear with minimum 90% at 10 years, and 80% at 25 years. Solar panel from Lorentz, Germany or European equivalent. |  |  |  | 0
2 | NYYf Cable for DC Connection: PVC insulated and PVC inner sheathed, Annealed Flexible Copper Conductor stranded cables shall be manufactured and tested according to relavent IEC/BDS/BS/VDE standards and as per detailed specification mentioned The work shall be carried out as per direction/approval/ acceptance of the Engineer. Providing & laying of PVC insulated & PVC Inner sheathed cable (NYYF) 1CX10.0 sqmm (For Solar PV Panel to DC Combiner Box to Inverter) | m | 300 |  | 0
3 | PV Combiner Box including bus bar, double pole DC circuit breaker, surge protector devices, etc. all complete as per instruction of Engineer In Charge | Set | 1 |  | 0
4 | Solar Submarsible Pump controller: Supplying, installation, testing & commissioning of 9.3 KW, 3-phase solar pump controller with heat sink assembly style. Controller shall also be protected for overload and over current protection from both DC and AC side. Controller shall be in accordance to the IEC 61800, EN, TUV or equivalent international standards and Engineer as per following specification : Country of origin: Schneider(Germany) / ABB( Italy) / Nastec(Italy) / Lorentz(Germany). Technical Data : I. Power KW: 9.3 KW II. Nominal Dc input Voltage:300-900VDC III. Nominal AC input Voltage:370-420VAC III. True sine wave inverter IV. Ac frequency: 50 Hz V. Integrated power point tracking VI. Operating temperature range:10 0C-50 0c. VII. Relative humidity: 5-95%,non-condensing VIII. Efficiency : minimum 99% IX. Noise <50 dB at 1m distance X. EMC filter: Integrated | Set | 1 |  | 0
| XI. Communication port : RS 485 / RS 232. shall have the option to be incorporated GPRS module remote monitoring system. XII. Degree of Protection: according to IP20 and IEC 60529. XIII. Protection: Shall have lightning induced current by surge protective device of adequate rating both in DC and AC side in parallel at the entry and exit terminal of the inverter. Shall also have over load and over current protection from both DC and AC side. overcurrent, overvoltage, undervoltage, overheating, default phase, overload, shortcut, etc., and also include water leverl sensor failure protection, full water, dry running, weak sunshine warning special protection functions for solar pump system. Could record the detailed running status during failure & has fault automatic reset function. XIV. Compliance : ISO9001 & ROHS (Restriction of Hazardous Substances) certified company & CE/UL marking Warranty: At least 03 yrs |  |  |  | 0
5 | Charge Controller: Supply fitting fixing of MPPT charge controller, high accuracy confirming certification by UL/ULC/VDC/VDE/ETL in accordance with the requirement of relevant IEC standards and shall have authentication to use CE, TUV and UL/ULC logo. Necessary catalogue, operation & maintenance manual will be supplied by the bidder. All complete & sample approved by Engineer-in-charge. Solar Charger: 12/24v, 20A Brand : SMA/Morning Star/Outback/apollo Origin : USA/Germany Warranty : At least 03 yrs. | Each | 1 |  | 0
6 | Solar Battery with casing: Supply, installation (with effictive connection), testing & commissioning of Solar battery with nominal voltage,12V,130AH or above@10HR or equivalent Deep Cycle heavy duty industrial type Lead Acid battery, positive plate: Tubular or solid thicker Plate, negative plate: Pasted float, Electrolyte Dilute Sulfuric Acid, specially suitable for Solar system. The term 32500"Solar" must be engraved at the body of Battery. Battery,12V,165AH Battery rack/cabinet of sufficient size Brand: Hamko/Volvo/Rahim Afrooz or equivalent Origin: Made in Bangladesh Warranty: At least 05 yrs. | Each | 1 |  | 0
7 | Solar Inverter for lighting load: Supply, fitting, fixing & testing the solar inverter, protected from lighting induced current by surge protective device of adequate rating both in DC and AC side in parallel at the entry and exit terminal of the inverter. The Inverter shall also be protected for overload and overcurrent protection from both DC and AC side. The inverter shall be tested and certified by UL/ULC/VDC/VDE/ETL in accordance with the requirement of relevant IEC standards and shall have authentication to use CE, TUV and UL/ULC logo. Solar Inverter: 500 watt 12 volt, Pure Sine Wave, Efficiency 94% (minimum), Brand: Outback / Extruder / Deutsche Power / Victor (Netharland), Origin : USA / EU, Warranty: At least 03 yrs. | Each | 1 |  | 0
8 | Providing & fixing 25.4 mm (1") dia 457 mm (1.5 ft) long solid copper rod with 6.6 mm thick 150 mm x 150 mm copper made base with sharp end top, fixed on the top of 2.0"( 2.5 - 3 mm thick ) dia 10' long GI pole by necessary accessories . The pole shall fixed on parapet wall with necessary CC work and other accessories for arresting lightning as per plan (enclosed) and as per direction of the engineer. [Fig : 4.19] | set | 2 |  | 0
9 | Providing & drawing no-2 HDBC wire through 12.7 mm. (½") dia G.I. pipe including fitting, fixing the G.I. pipe in wall or column complete as required. | m | 60 |  | 0
| Civil works |  |  |  | 0
| Earth Excavation | cum | 96 |  | 0
19 | One layer brick flat soling | sqm | 48 |  | 0
20 | R.C.C Works in Individual Footing | cum | 14.4 |  | 0
21 | R.C.C Works in Column Padestal | cum | 3.84 |  | 0
22 | R.C.C Works in Column | cum | 3.84 |  | 0
23 | Shuttering Works in Footing | sqm | 28.8 |  | 0
24 | Shuttering Works in Column Padestal | sqm | 38.4 |  | 0
25 | Shuttering Works in Column | sqm | 38.4 |  | 0
26 | Grade 400 (B400DWR / B420DWR: complying BDS ISO 6935-2:2016 / ASTM A615) | kg | 1565.28 |  | 0 | 305.28
27 | Anchor Bolts & Nut, Base Plate | kg | 686.967 |  | 0 | 26.6667
28 | I Joist /Column | kg | 4015.2 |  | 0 | 267.84
29 | Supply, fabrication and installation of hot rolled structural grade steel angle in truss or any form of structure of any thickness conforming to ASTM A36 with a minimum yield strength of 250 MPa, including the cost of testing, application of red/grey-oxide primer etc. all complete as per drawing, specification and direction of Engineer-in-charge. |  |  |  | 0 | 1068.48
30 | 75 mmX75mmX5mm Angles | kg | 1202.92 |  | 0 | 992.16
31 | 25 mmX25mmX4mm Angles | kg | 1199.15 |  | 0
| 50 mmX50mmX5mm Angles | kg | 452.4 |  | 0
| GENERAL GUIDELINES/CRITERIA FOR SOLAR SYSTEM: |  |  |  | 0
| I.The bidder shall examine the site before the design of solar system & its components II.The bidder shall have facilities and proper tools and machineries for installing, testing & commissioning of solar panel. III.Adequate space & height shall be provided in the rows of panels for easy air flow to avoid excessive heat generation in the panel and to provide access for rain water drainage and damage to protect from dirty water. Minimum air gap between two panels shall be 25 mm. |  |  |  | 0
| IV.All frames of the PV module, combiner box, inverter etc. shall be equipotential bonded and earthed with the building earth electrode which is conventional and / or chemical electrode system with soil conductivity enhancing material that the earth resistance must be less than 1 Ohm as per related standard and code of practice. |  |  |  | 0
| V. The solar panel mounting shall be of galvanized iron or equivalent to ensure rust protection of the installation. All nut bolts shall be of stainless steel (SS) or galvanized mild steel (MS) materials. VI. After successful completion, testing & commissioning of the whole system the contractor shall have to train nominated person(s) of the user for a period of at least 2 days. VII. After completion of whole system and before handing over the system to the concerned authority, the contractor must have to provide minimum 30 days' satisfactory operation for performance evaluation. |  |  |  | 0
| VIII. Technical specification with catalogue of PV module, inverter must be submitted with technical offer. IX. Only approved cable shall be used for wiring. X. Sufficient AC and DC circuit breakers shall be used to ensure proper safety of the system. |  |  |  | 0
| Total |  |  |  | 0

## Part_C3
Part C3: Electrical Works
Sl | Description of Works | Unit | Qty. | Unit Price (BDT) | Total Price (BDT)
1 | Supplying and fixing of almirah type 18 SWG metal board With water tight arrangement of depth 228mm (6”) duly painted with powder coating with epoxy polyester resin on all surfaces of board (gray / off-white) having built in push type / suitable locking arrangement including metal bridges of suitable size for fixing of all electrical control devices complete with suitable anchoring arrangement in wall / column and keeping provision for cable inlets and exits as required (only front surface of the board will be considered for measurement) accepted/approved by the Engineer-in-charge. | sqm | 0.5 |  | 0
2 | Providing & fixing on a prepared board 500 volt grade following triple-pole molded case circuit breaker (TPMCCB) with thermal over-current and instantaneous electromagnetic short circuit release provision, Manufactured / Assembled and tested in accordance with IEC / VDE / NEMA / BS / JIS along with relevant BDS IEC standard. TPMCCBs accepted / approved by the Engineer-in-charge. 63 Amps. (Minimum 10-KA) | Each | 2 |  | 0
3 | Providing and fixing 500 V 3-phase bus bar system assembled in prelaid board with porcelain insulators. There will be equal size holes on every bar at 0.5" interval and bar to bar gap shall be 2" - 3". Copper flat bar (5 nos) : 4 nos 15"x1"x8mm and 1 no 4"x1"x8mm for earthing mounted on insulator at both ends individually. | Each | 1 |  | 0
4 | Providing & fixing 250V, 50 Hz grade following concealed type sub-distribution board made of 18-SWG MS sheet complete with hinged type door, built-in type locking arrangement, one no. 60 A capacity bus-bar with required no. of holes thereon on insulators at both ends, copper blocks for neutral and earth terminal, SPMCBs Manufactured / Assembled and tested in accordance with IEC / VDE / NEMA / BS / JIS along with relevant BDS IEC standard having minimum breaking capacity 6 / 10-KA with thermal over current and instantaneous electromagnetic short circuit release, necessary arrangement for fixing of MCBs duly painted with powder coating with epoxy polyester resin on all surfaces of board (gray / off-white) etc. In front side there will be tempered thick fiber glass of minimum 8 mm thickness with rubber gaskets etc. with SPMCBs accepted / approved by the Engineer-in-charge. 4-Way SDB (with box size minimum 220mmx 132mmx148mm) in-coming : 1 x 30 amps (6 KA) & out-going :4 x 5 / 10 / 15 amps SPMCB (6 KA) . | Each | 1 |  | 0
5 | Concealed conduit wiring with the following PVC insulated stranded cable (BYA) & PVC insulated Green / White color ECC wire (BYA) through PVC conduit of reputed manufacturer complete with 18 SWG GP sheet pull box with 3mm thick ebonite sheet cover, fixing materials, other accessories etc. as required including mending the damages good. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) and cables shall be manufactured and tested according to relevant IEC / BDS / BS / VDE standards and as per detailed specification mentioned in Annexure-1. The work shall be carried out as per direction & approval of the Engineer. Cables manufactured by govt. of Bangladesh owned / shared company ltd. (Eastern cables) approved by the Engineer. Cables manufactured by govt. of Bangladesh owned / shared company ltd. (Eastern cables) approved by the Engineer. 1C-2x2.5sqmm (BYA) cable with 2.5sqmm (BYA) ECC wire through PVC pipe of minimum inner dia 16 mm having wall thickness of 1.5 mm | m | 15 |  | 0
6 | CONCEALED CONDUIT POINT WIRING |  |  |  | 0
| Concealed conduit wiring for following point looping at the switch board with earth terminal with 1C-2x1.5 sqmm PVC insulated cable (BYA) & same size PVC insulated ECC(BYA) Green / White color including circuit wiring with IC-2x2.5 sqmm PVC insulated cable (BYA) & same size PVC insulated ECC (BYA) (Green / White color) through PVC conduit (one conduit from switch board to common point on ceiling is considered to draw 3 pair of cable) of reputed manufacturer) of minimum 25 mm dia & 1.5 mm wall thickness complete with 18 SWG GP sheet / PVC switch board pull box with 3mm thick ebonite sheet cover, fixing materials etc.(without switch) as required including mending the damages good. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) and cables shall be manufactured and tested according to relevant IEC / BDS / BS / VDE standards and as per detailed specification mentioned in Annexure-1. The work shall be carried out as per direction & approval of the Engineer. Cables manufactured by govt. of Bangladesh owned / shared company ltd. (Eastern cables) approved by the Engineer. |  |  |  | 0
6.1 | Light / exhaust or wall bracket fan point | Point | 7 |  | 0
6.2 | Fan point | Point | 1 |  | 0
7 | Providing & fixing 250 volt single phase 13 / 15 / 16 / 20 Amps. 3-pin combined switch socket outlet (surface / Concealed type) manufactured and tested in accordance with relevant IEC / VDE / NEMA / BS / JIS standards mounted on required size 18 SWG galvanized plain sheet board / Plastic Board (Self-extinguishing 650oC) of 76.2 mm. (3") depth. (Manufacturer shall have certificate of standard which they follow). Made in HONGKONG/ MALAYSIA / SINGAPORE / S KOREA / THAILAND | Each | 1 |  | 0
8 | Providing & fixing 250 volts. 5 / 6 amps (minimum) concealed type following switch / switch socket manufactured and tested in accordance with relevant IEC / VDE / NEMA / BS / JIS standards mounted on required size 18 SWG galvanized plain sheet / PVC board (Self-extinguishing 650oC) of 76.2 mm (3") depth. All electrical contacts shall be of brass / copper. Made in ENGLAND / GERMANY / JAPAN / USA or EU countries. |  |  |  | 0
8.1 | Four gang switch | Each | 2 |  | 0
8.2 | One gang switch & one 5 amps. 2-pin socket combined | Each | 1 |  | 0
8.3 | Gang type Fan Regulator. Assembled and made in BANGLADESH / CHINA / INDIA / TURKEY / VIETNAM | Each | 1 |  | 0
9 | Ceiling Fan & Related fittings |  |  |  | 0
9.1 | Supplying & fixing AC capacitor type ceiling fan (without regulator) 1442 mm. (56") Sweep, Input power : Maximum 65 watt. of following specifications and sizes complete with minimum 305 mm (1 ft) long and 0.75 -1.0" dia, 2.3 mm thickness MS pipe down rod, tempered cast aluminum blades, 2.5 µf 400V AC capacitor, canopy, double Z ball bearing, best quality silicon sheet core, best quality copper made super enamel wire, aluminum alloyed casting body / metal body having safety pin with powder coated heat / docu paint as required as per BDS 818 etc. connecting PVC wire complete as required. Rated voltage : 230 volts Rated frequency : 50 Hz Rated speed : 300 rpm ± 5 % Service value : Minimum 3.5 m3 / min / watt Temperature rise : Maximum 55ºC Class of Insulation : Minimum E Noise level : Maximum 60 dB at a distance of 1 meter. | Each | 1 |  | 0
9.2 | Providing & fixing U type fan clamp made of 12 mm. dia MS rod having at least 750 mm clearance around and shall be placed above the MS rod mesh of the roof slab including necessary bolts, nuts etc. as required as per sample approved by the Engineer. | Each | 1 |  | 0
10 | Providing & fixing of the fancy bracket light Fittings with carrier, brass holder, earth terminal, necessary wiring with 2 x 0.4 sq.mm stranded PVC insulated flexible FR cable etc. The fittings shall be suitable for use of LED lamp and complete sample to be accepted / approved by the Engineer-in-charge (with 2 years warranty). Light source: 1x12W LED Bulb Material: SS pipe (Size-30*30mm, thick- 1.2mm) & SS Sheet body, Alu Sheet, MS Sheet, Glass. L-100mm, H-220mm, P-120mm GLORIA cat. no. GWBL-2505-2861 Energy+ Cat No EPWL-30003 Cosmo Cat No-BDTCLGWB-01 Asha Cat No-ACS-BS-1221 G57 Crescent-CB-1802/1 or equivalent. | Each | 6 |  | 0
11 | Supply & fixing spot/Panel 18 W, Approximate Dia -218 mm LED light fittings of following specifications: Luminous efficacy: i)For Spot/Bracket LED Light Fittings: 80 lm/W (min), ii)For Panel/Tube Light Fittings: 100 lm/W (min) Power Factor: minimum 0.95 Color Rendering Index(Ra) : i) For Residential building Ra≥80 ii) For office and other types of buildings 70≤Ra<85 Driver: Should be of IEC standard such as MEANWELL/OSRAM/ENERGY+/SIGNIFY(PHILIPS) or equivalent LED chips :EPISTAR / OSRAM / SIGNIFY(PHILIPS) / CREE / BRIDGELUX or equivalent. Color temperature : 3500K-6500K (Warm-White) Model & sample to be accepted / approved by the Engineer-in-charge (with 2 years warranty). Round panel (surface type) Material: Alu Alloy, Acrylic Gloria Cat No-GSDL-513 Energy + cat No-EPPLLED-2006 Cosmo cat no-BDTCL-LSRPL-01 Adex-AD SDL 830/840/865 Asha Cat no- ACS LPL-1451 Megaman-MXTL1013-Y Walton WLED-DSPLR-200-UL or equivalent. | Each | 4 |  | 0
12 | Supply 68 pcs Hand Tool Set Industrial including Hex Key with Ball-9Pcs, 1.5- 10mm CrV (YT-0505); Socket 1/4" 6PT CV Regular (4MM- YT-1401, 4.5mm- YT-1402, 5mm- YT-1403, 5.5mm- YT-1404, 6mm- YT-1405, 7mm- YT-1406, 8mm- YT-1407, 9mm- YT-1408, 10mm- YT-1409, 11mm- YT-1410, 12mm- YT-1411, 13mm- YT-1412; Tweezers 140mm (YT-6903); Electrician's Knife (YT-7601); Adjustable Wrench 6" 150 mm (YT-2071); Long Nose Pliers 160mm Insulated 1000V (YT-21154); Side Cutting Pliers 160mm Insulated 1000V (YT-21158); Measuring Tape 3mx16mm Nylon (YT-7150); Automatic Wire Stripper 175mm (YT-2268); Voltage Tester (YT-2861); Aluminum LED Torch, 9LED, Material Loop, Rubber Button, Color: Black (YT-08570); Utility Knife 9mm SK2 (YT-7502); Electrical Insulation Tape PVC 0.13mm 19mmx20m Black (YT-8165); Spinner Handle 1/4'' DR. (YT-1427); Digital Millimeter (YT-73080); Desoldering Pump 19.5x190mm (YT-82742); Bit Adapter 1/4''x1/4" (YT-1297); Insulated Screwdriver 1000V 4x75mm (YT-2816); Insulated Screwdriver 1000V 5.5x125mm (YT-2818); Insulated Screwdriver PH1x80mm (YT-2822); Insulated Screwdriver PH2x100MM (YT-2823); Precision Screwdriver Set 6Pcs S2 (YT-25861); Soldering Iron 30W (YT-8271); Soldering Wire; Screwdriver Bits 20PCS; Aluminium LED Torch (9 LED, Material Loop, Rubber Button, Color: Black) which brand of Yato Brand YT-39009/equivalent | Per set | 1 |  | 0
13 | Earthing & Construction Pit |  |  |  | 0
13.1 | Earthing the electrical installation with 40 mm (1.5") dia G.I. pipe (earth electrode) having 6.35 mm. dia hole across the pipe at 305 mm. interval securely bonded by soldering with 2 nos. of No-2 SWG HDBC earth leads (at the top of the electrode) with its protection by 20 mm. (3/4") dia G.I. pipe up-to plinth level run at a depth of 609.6 mm (2 ft) below G.L up-to main board to be earthed including necessary connecting copper sockets, bolts, nuts, etc. complete for maintaining earth resistance within 1 ohm. Depth of bottom of main electrode at 19050 mm. (62.5 ft) from GL & length of electrode 18288 mm. (60 ft). | Per set | 4 |  | 0
13.2 | Construction of earthing inspection pit inside measurement 600 mm x 600 mm with 250 mm thick brick in cement mortar (1:4) with 100mm thick RCC top slab (1:2:4) with 1% re-enforcement 450 mm dia water sealed CI man-hole cover with locking arrangement including necessary earth works, site filling and one brick flat soling 75 mm thick (1:3:6) base concrete for making inlet channel & 12mm thick (1:2) cement plaster with neat finishing etc. all complete up to a depth of .75 meter. | Per set | 4 |  | 0
| Total Amount, BDT |  |  |  | 0

## Sheet1 (hidden)
E1. ESMP Implentation Cost
Sl | Description of Works | Unit | Qty. | Unit Price (BDT) | Total Price (BDT)
1 | Providing and maintaining Semi pucca standard labour shed as per the drawing approved by the E.I.C. ( seperate for Male & Female) including temporary isolation facilities for suspected workers infected with Covid-19 in case of emergency, within the vicinity of the sub-project sites with necessary pipe water supply/ hand tube-well, toilet, kitchen, installing safe drinking water dispensers with one-time cups / plates / glasses (workers should be encouraged to carry individual cup / plate / glasses for their own use) and lighting/ power facilities all complete including removal of structures and clearing the site on completion of the work. All materials and equipment shall be the property of the contractor. The contractor shall submit for the approval of the Engineer the detailed plans and drawings of the labor sheds. Minimum plinth area : 100 sqm each or its fractional multiples (Fixed) | month | 10 | 15000 | 150000
2 | Providing Water supply facilities for the labor shed and work site by supplying, fitting & fixing of 1 no. centrifugal pump with the test tube-well installed for that scheme by the contractor as per instruction of EIC | each | 1 | 25000 | 25000
3 | Sanitation facilities (at the labor shed): 2 nos. of the toilets preferably portable toilets (1 no. for women and 1 no. for men) including wash basin, plastic water tank, plastic tap (Bib cock), hand wash liquid soap /soap etc. | each | 2 | 50000 | 100000
4 | Dust suppression measures by water spraying throughout the construction period in and around the sub project site, uncovered aggregates and loose materials such as stockpiles of the sands, excavated earth etc. daily or as per requirements (lump sum) | month | 10 | 7500 | 75000
5 | Masonry pucca ( providing brick soling and net cement finishing) platform or movable wooden platform (it should be impervious) at least 100 sft. size), for keeping fuel and lubricants for machineries. | LS | 1 | 50000 | 50000
6 | Establish cautionery sign board, health & safety signs, COVID-19 safety sign and preventive messages , caution tape. Setup complain box and hanging of GRM flow chart on panaflix. GRM record Register and minutes books at union level. | LS | 1 | 20000 | 20000
7 | Providing necessary facilities in construction site for maintaining site safety of 30 nos construction worker including safety helmet, safety belt , apron, gumboot, goggles etc. | Job | 1 | 50000 | 50000
8 | Providing necessary facilities in construction site for maintaining site safety of 10 nos construction inspection team member including safety helmet, safety goggles, safety shoe etc. | Set | 1 | 35000 | 35000
9 | Supplying and providing of first aid box with necessary materials/medicine (hygienic gown, thermometer, adhesive dressings, antiseptic solutions, bandages, cotton balls or swaps, emergency blanket, gloves, hand sanitizer, mask, ice pack, saline etc ). All complete as per direction of Engineer-in -charge. | each | 1 | 3500 | 3500
10 | Installing fully restricted fencing at every construction site with marking tape (Using optimum-grade polyethylene, these tapes are manufactured and are demanded for civil, construction work warning text and symbols of safety. Additionally, these tapes are available in different colors, languages, designs and sizes) for construction site with clearly written warning notices for adjacent communities, as well as clearly marking at entry/ exit gates for workers as per Engineer-in-charge. (To be continued for total constrution period). | LS | 1 | 20000 | 20000
11 | Wastes disposal facility during the construction period; collection, transportation and disposing wastes in/c providing separate bin for organic & inorganic waste (To be continued for total constrution period). | LS | 1 | 15000 | 15000
| Total Amount, BDT |  |  |  | 543500

## Details of Cost Reduction (hidden)
Cost Reduction Details
Item No | Description of Items | Previous Amount in BDT | Revised Amount in BDT | % of Cost Reduction | Remarks
Part A | Production Tubewell (PTW) at Potibunia | 3835576.585 | 3835576.585 | 0%
Sub-Total of Part A |  | 3835576.585 | 3835576.585 | 0%
Part B | Civil Works
Part B1 | Pump House Building at Potibunia
| Concrete stairs have been replaced by prefabricated M.S ladder. On the first floor, cantilever portion has been omitted. Side wall has been replaced by MS railing at 1.0 meter height. At the roof, solar provision for internal use and the space for O&M works have been reduced; the floor area has been re-adjusted accordingly | 4795484.1528 | 3875363.8806 | 19.19% | Adapting a pump house building to a simplified structure tailored to the local context.
The other part of the pump house building are remaining same
Part B2 | Site Master Plan at Potibunia
| Boundary wall has been replaced by simple fencing with necessary columns | 814867.02 | 47276.24 | 94.2% | Contemplating the implementation of a straightforward fencing solution instead of a substantial boundary wall.
| The other parts are remaining same | 520099.6431 | 520099.6454 | -4.423e-07%
Part B3 | Tank Site at Camp 16 Block A (With Site Protection Works) | 495913.9401 | 495913.9401 | 0%
Part B4 | Tank Site at Camp 16 Block C | 569549.3806 | 569549.3806 | 0%
Sub-Total of Part B |  | 7195914.1366 | 5508203.0867 | 23.45%
Part C | Electro-mechanical Works
Part C1 | Mechanical Works (Submersible and Chlorine Pump with Accessories) | 900852 | 900852 | 0%
Part C2 | Solar System Works (Main Energy Source) | 2300313.04 | 2300313.04 | 0%
Part C3 | Electrical Works | 310823 | 310823 | 0%
Part C4 | Transformer for Electricity Network Connection (Backup Energy Source) | 541739 | 541739 | 0%
Part C5 | Generator (Optional Energy Source) | 1016467 |  | 100% | The primary energy source is envisioned to be a solar system, with the electricity network serving as a backup energy source.
Sub-Total of Part C |  | 5070194.04 | 4053727.04 | 20.05%
Part D | Water Networks, House Connections & Tap Stands and Water Tanks
Part D1 | Water Network, HDPE PN 8, SDR 21 (with Valves and Chambers)
D1.1 | Water Distribution Network at Potibunia | 4147101.5591 | 1509065.251 | 63.61% | The previous cost was determined using standard practices for PN10 HDPE pipe and considering in molded fittings. However, the rate has been revised to align with local practices, PN 8 HDPE pipes and adhere to the guidance provided by UNICEF. Additionally, the diameter has been modified from 160mm to 125mm for transmission main and distributon main of Potibunia host community.
D1.2 | Water Distribution Network at Camp 16 Block A | 1651195.7408 | 2232497.8745 | -35.2%
D1.3 | Water Distribution Network at Camp 16 Block C | 1034306.3515 | 52801.2851 | 94.9%
D1.4 | Water Transmission Network from PTW to Camp 16 Block A&C | 3404175.0699 |  | 100%
Sub-Total of Part D1 |  | 10236778.7213 | 3794364.4105 | 62.93%
Part D2 | House Connection and Tap Stand with Water Meter
D2.1 | House Connection with Water Meter at Potibunia Host Community (126 Nos.) | 3749813.68 |  | 100% | A basic water meter chamber has been incorporated as an essential component of the house connection tap stand, consolidating it rather than having a separate chamber. Additionally, a single tap has been chosen instead of two for each house connection, with the aim of streamlining costs..
D2.2 | Tap Stand with Water Meter at Camp 16 Block A&C (30 Nos.) | 964215.9587 | 673972.3135 | 30.1% | A simple water meter chamber has been considered as an integral part of tap stand, instead of separate chamber.
Sub-Total of Part D2 |  | 4714029.6387 | 673972.3135 | 85.7%
Part D3 | Water Tank with Piping & Valve Arrangement (Potibunia and Camp 16 Block A&C)
D3.1 | Food Graded Plastic Overhead Water Reservoir | 937232 | 937232 | 0%
D3.2 | Piping & Valve Arrangement at Water Tank Site | 550573 | 398780 | 27.57% | PN 8 pipes have been chosen for required lengths instead of PN 10. 50mm HDPE ball valve is now chosen for the water tank drainage system, replacing the Brass Gate Valve for the cost reduction purpose.
Sub-Total of Part D3 |  | 1487805 | 1336012 | 10.2%
Part E | Others
Part E1 | ESMP | 180664 | 180664 | 0%
Part E2 | O&M | 474800 |  | 100% | May consider with O&M cost of the project, instead of Capital Cost
Part E3 | Office Furniture | 105000 |  | 100% | May consider with O&M cost of the project, instead of Capital Cost
Part E4 | Insurance | 336462.0375 |  | 100%
Sub-Total of Part E |  | 1096926.0375 | 180664 | 83.53%
Grand-Total (Summation of Sub-Total of Part A, B, C, D and E) |  | 33637224.1591 | 19382519.4358 | 42.38% | Total Cost Reduction: 89,73,540.16 BDT
Total Cost Reduction: 14254704.72 BDT