## Production BH
Bill of Quantities for Installation of Production Borehole
Sl. No. | Description of Items | Unit | Quantity | Unit Rate (in BDT) | Total Amount (in BDT) | #REF!
1 | Mobilization, transportation, relocaton of temporary structure and preparation for installation of 200 mm dia. production tubewell including supplying and local transportation of complete drilling equipments viz drilling rig, compressor, mud pump, electric or diesel or petrol generator, drilling pipe, electric cable etc. to the work site, installation of electricity, water supply, labor shed, site office and store, digging mud pit etc. and cleaning , leveling, dressing the work site after completion of the work all complete as per specification and direction of the Engineer-in-Charge. | LS | 1 |  | 0
2 | Drilling to Desired Depth: Execution of drilling through all sorts of strata by reverse circulation / rotary drilling method with supply of automatic truck mounted drilling rig / any other device appruved by EIC, for making 500 mm dia. vertical holes up to required depth by supplying and using of bentonote as a drilling fluid including collection of soil strata at every 3 meter interval and every change of formation, preserve the soil samples in boxes, recording penetration rate etc. all complete as per direction of EIC.
| i) 0 m to 50 m depth | m | 60 |  | 0
| i) 51 m to 100 m depth | m | 60 |  | 0
| i) 101 m to 200 m depth | m | 130 |  | 0
| i) 201 m to 250 m depth | m | 60 |  | 0
3 | Geophysical logging (SP and resistively LN & SN) and Gamma logging (Lithology/Soil type) up to the target drilled depth and submission of log sheet with interpretation etc. All complete as per direction of the authorized representative of UNICEF including carrying and all taxes etc. (optional only if geophysical borehole logger is available). | Item | 1 |  | 0
4 | Material of Well: Supply and installation / lowering of the following tubewell components including jointing checking verticality from time to time including testing etc. complete as per direction of Hydro-geologist / EIC.
| i) Sand - trap : 200 mm dia uPVC Casing sand trap in full section with 12.60-14.50 mm thick | m | 3 |  | 0 | 0 | 0
| ii) Strainer : 200mm uPVC screen with 12.60-14.50 mm thick | m | 30 |  | 0 |  | 0
| iii) Blind pipe : PVC Blind pipe of 200 mm dia. with 12.60-14.50 mm thick | m | 214 |  | 0 |  | 0
| iii) MS Cap : 200mm dia. 4mm thick top MS cap | nos. | 1 |  | 0 |  | 0
5 | Centralizer: Supply and fixing of centralizes made of 12mm MS bar to casing and screen at each joint approximately at 6m intervals as per design and direction of the Engineer. | Each | 15 |  | 0
6 | Gravel packing: Preparation for gravel pack with supply of gravels of approved gradation and quality including sieving for designed gradation, cleaning , washing etc. and pouring gravels through the annular space up to the level not less than 15 meters above the upper most part of the screen or up to the bottom of an existing impervious/semi-impervious layer including complying with the pouring method laid down in the specification and sounding of gravel pack from time to time all complete as per direction of Hydro-geologist / EIC. | Cum | 15 |  | 0
7 | Borehole Filling: Filling the borehole around the well from top of shrouding to GL as per the direction of the hydrogeologist/EIC | rm | 200 |  | 0
8 | Sealing the annular space around the well casing with clay balls made of 50% local puddle clay and 50% bentonite 3.00 meter thick at the top gravel pack as per specification, drawing, design and direction of the Engineer-in-Charge. | LS | 1 |  | 0
9 | Development: Development by over pumping, surging and backwashing in 3 stages by using suitable capacity air compressor and submersible pump for removing mud-cakes from borehole wall including supply of development material all complete till water is sand and turbidity free as per specification and direction of the Hydro-geologist / PTP
| i) Development by air lift pumping and surging with air compressor | LS | 1 |  | 0
| ii) 1st chemical treatment (20 kg bleaching powder) 2 days | LS | 1 |  | 0
| iii) Development by high capacity (20 m3/hr) with disel engine and submersible pump (1 day) | LS | 1 |  | 0
10 | Step Draw Down Test: Conducting 4 step draw down test for 2 hours(2x4) using pump of variable discharges as per direction of Hydro-geologist / EIC. | Hour | 8 |  | 0
11 | Pumping Test: Long term continues (non- stop) pumping test of the well for 24 hours at sand and turbidity free water by a required capacity engine driven submersible pump including supply of all materials, equipment, consumables, labors etc. required for pumping test including a 24 hours recovery, all required information shall be recorded all complete as per direction of Hydro-geologist / EIC. | Hour | 72 |  | 0
12 | Sanitary Sealing: Making sanitary seal up to 2m depth from GL to the top of puddle clay at 300 mm away from housing of PTW with CC including supply of approved quality cement, sand and stone chips (13 mm down graded)in ratio 1:2:4 with 3% bentonite, all complete as per contract and as per direction of EIC. | Cum | 3 |  | 0
13 | Water Quality Testing. Collection of water sample in a DPHE recommended sampling bottle and conduct laboratory testing for water quality on 8 parameters; a) Cloride (Cl), b) Iron, c) Arsenic (As) , d) PH, e) Turbidity f) TC g)FC h) E-Coli | Set | 1 |  | 0
| Total |  |  |  | 0