## Well Development
BoQ for the Development work including Pump Test of Existing Production Well (DPHE Borehole)
Item No | Description | Unit | Qty | Rate (Tk) | Total Amount (BDT)
A Mobilization
A1 | Mobilize and transport all equipments, tools and necessary materials to the sites as per technical specification and direction of the authorized representative. Demobilize the same on completion of the work and clean the site as per technical specification. | LS | 1 |  | 0
Sub-Total |  |  |  |  | 0
B: Tube Well Development
B1 | Washing with Dispersant and Chlorination: Preparing a solution of sodium hexametaphosphate (Calgon) or other approved dispersant mixed together with dry and loose calcium hypochlorite powder (Bleaching Powder) containing 65% available chlorine, washing the well screen slots, the gravel pack and the wall of the drilled hole using the solution, placing the solution by tremie pipe throughout the full length of the well screen for 24 hours, etc. all complete as per Technical Specification and accepted by authorized representative. Measurement shall be taken in cubic meter for the volume of water in the well.
B1.1 | Washing with Dispersant. | LS | 1 |  | 0
B2 | Compressed Air Primary wash: washing by developing developing a pressure of at least 320 psi using compressor. The development will start with setting the educator pipe at the mid-point of the lowest screen segment and raised upward slowly one after another screen segment until the highest screen segment is reached. At each mid-point position, compressed air will be pumped for 10 minutes at a time before cleaning the water discharge valve to initially back washing.
B2.1 | Compressed Air Primary wash | LS | 1 |  | 0
B3 | Development by High Velocity Water Jetting (Based on site Condition): Carrying out high velocity water jetting by jetting tool which is capable of discharging horizontally at a rate of 100 meter per second velocity from four opposite nozzles using 75mm diameter jetting head and 50mm diameter jetting pipe inside the screen, all complete including preliminary washing, alternate surging, pumping, backwashing, etc. in accordance with Technical Specification and accepted by the authorized representative. Measurement shall be taken in linear meter for the length of screen inside the well.
B3.1 | Water jetting in/c alternate surging, backwashing. | LS | 1 |  | 0
B4 | Development by Over Pumping: Carrying out step pumping at increasing rates from 75% to 150% of design capacity of the tube well by installing a high capacity pump of about 60 m3/hour with 45-60 meter head or required head for a minimum of 8 hours, all complete in accordance with Technical Specification and accepted by the authorized representative. Measurement shall be taken in hours to complete the development by over pumping.
B4.1 | Development by over pumping | LS | 1 |  | 0
B5 | Step Drawdown Test: Carrying out step drawdown test at 75%, 100%, 125% and 150% of the design well capacity for 1.5 hours continuous pumping at each step including discharge measurement, water level measurement, sand test, recording of test results, water testing, etc.all complete in accordance with Technical Specification and accepted by the authorized representative. Measurement shall be taken in hours to complete the step drawdown test.
B5.1 | Step drawdown test including all measurement. | Hour | 8 |  | 0
B6 | Continous Discharge Test and Recovery Test: The constant discharge test at the design well capacity for 8 hours continuous pumping including discharge measurement, water level measurement, sand test, recording of test results, water testing, etc.all complete in accordance with Technical Specification and accepted by the authorized representative.
B6.1 | Continous pumping test, Recovery Test including all measurement | Hour | 72 |  | 0
B7 | Disinfecting the Tube Well: Carrying out disinfecting the tube well by placing Calcium Hypochlorite Powder (Bleaching Powder) in a container, lowering and raising the container through the full depth of the well, etc. all complete in accordance with Technical Specification and accepted by the authorized representative.
B7.1 | Disinfecting the Tube Well. | LS | 1 |  | 0
Sub-Total |  |  |  |  | 0
C: Water Quality Test
C1 | Water quality parameter test as per technical specification | LS | 1 |  | 0
Sub Total |  |  |  |  | 0
Sub-Total Cost (A+B+C+D) |  |  |  |  | 0
VAT and IT (10.5% of Sub-Total Cost) |  |  |  |  | 0
Total Cost (Including VAT & IT) |  |  |  |  | 0

## Part_B2D (hidden)
Land Development, Landscaping & Plantation
Item SL. | PWD SOR 2022 | Description of Items | Unit | Quantity | Unit Rate (BDT) | Amount (BDT)
Part-4: Land Development, Landscaping & Plantation
1.01 | 25.1 | Labour charge for scraping lawn surface up to 38 mm depth by spade, picking up all sorts of brick bats, rubbish by suitable tools, removing the same by head load or by any other means and stacking the same to a safe distance beyond 300 m including supply of tools and plants etc. all complete and accepted by the Engineer-in-charge. | sqm | 60.5 | 20 | 1210
1.02 | 25.2 | Preparation of ground to make ready for plantation by spading the ground to a depth of 150 mm to 230 mm beyond 38 mm deep scrapped ground by spade, breaking earth clods to powder by hammers, picking up all sorts of rubbish, unwanted grasses by suitable tools, carrying and spreading the surplus earth into low lying area including supply of tools and plants etc. all complete and accepted by the Engineer-in-charge. | sqm | 60.5 | 30 | 1815
1.03 | 25.3 | Leveling and dressing of lawn area to proper slope and grade by spading the same including supplying tools and plants etc. all complete and accepted by the Engineer-in-charge. | sqm | 60.5 | 10 | 605
1.04 | 25.4 | Supply of best and approved quality alluvial loamy silty soil including loading, unloading at both ends, properly stacking at site including supply of tools and plants etc. all complete and accepted by the Engineer-in-charge. | cum | 18.15 | 1100 | 19965
1.05 | 25.5 | Supply well decomposed cow dung carried by trucks or any other means including loading, unloading at both ends, stacking the same at site including supply of tools and plants etc. all complete and accepted by the Engineer-in-charge | cum | 3.025 | 2042 | 6177.05
1.06 | 25.6 | Labour charge for spreading the alluvial loamy silty soil from the stacks at site on the lawn surface, leveling, dressing the same including supply all necessary tools and plants etc. all complete and accepted by the Engineer-in-charge. | cum | 18.15 | 230 | 4174.5
1.07 | Analysis | Planting different types of tree plants one year old 1m high with vigourous canopy& stright trunk in/c carriage (Amloki ,hotoki, bash , panchutia., pata, bohera, ashothoBot, tulsi, ulot kombal, bell,, mango, jam , sofeda, gab, kodbell, chalta, boroi, lotkol, jamrul etc ,nagachua, kat golap, bottle brush. krishnochura, kamini, jolpi, nim ) | each | 20 | 220 | 4400
[5 empty] | Total | 38346.55

## Sheet1 (hidden)
E1. ESMP Implentation Cost
Sl | Description of Works | Unit | Qty. | Unit Price (BDT) | Total Price (BDT)
1 | Providing and maintaining Semi pucca standard labour shed as per the drawing approved by the E.I.C. ( seperate for Male & Female) including temporary isolation facilities for suspected workers infected with Covid-19 in case of emergency, within the vicinity of the sub-project sites with necessary pipe water supply/ hand tube-well, toilet, kitchen, installing safe drinking water dispensers with one-time cups / plates / glasses (workers should be encouraged to carry individual cup / plate / glasses for their own use) and lighting/ power facilities all complete including removal of structures and clearing the site on completion of the work. All materials and equipment shall be the property of the contractor. The contractor shall submit for the approval of the Engineer the detailed plans and drawings of the labor sheds. Minimum plinth area : 100 sqm each or its fractional multiples (Fixed) | month | 10 | 15000 | 150000
2 | Providing Water supply facilities for the labor shed and work site by supplying, fitting & fixing of 1 no. centrifugal pump with the test tube-well installed for that scheme by the contractor as per instruction of EIC | each | 1 | 25000 | 25000
3 | Sanitation facilities (at the labor shed): 2 nos. of the toilets preferably portable toilets (1 no. for women and 1 no. for men) including wash basin, plastic water tank, plastic tap (Bib cock), hand wash liquid soap /soap etc. | each | 2 | 50000 | 100000
4 | Dust suppression measures by water spraying throughout the construction period in and around the sub project site, uncovered aggregates and loose materials such as stockpiles of the sands, excavated earth etc. daily or as per requirements (lump sum) | month | 10 | 7500 | 75000
5 | Masonry pucca ( providing brick soling and net cement finishing) platform or movable wooden platform (it should be impervious) at least 100 sft. size), for keeping fuel and lubricants for machineries. | LS | 1 | 50000 | 50000
6 | Establish cautionery sign board, health & safety signs, COVID-19 safety sign and preventive messages , caution tape. Setup complain box and hanging of GRM flow chart on panaflix. GRM record Register and minutes books at union level. | LS | 1 | 20000 | 20000
7 | Providing necessary facilities in construction site for maintaining site safety of 30 nos construction worker including safety helmet, safety belt , apron, gumboot, goggles etc. | Job | 1 | 50000 | 50000
8 | Providing necessary facilities in construction site for maintaining site safety of 10 nos construction inspection team member including safety helmet, safety goggles, safety shoe etc. | Set | 1 | 35000 | 35000
9 | Supplying and providing of first aid box with necessary materials/medicine (hygienic gown, thermometer, adhesive dressings, antiseptic solutions, bandages, cotton balls or swaps, emergency blanket, gloves, hand sanitizer, mask, ice pack, saline etc ). All complete as per direction of Engineer-in -charge. | each | 1 | 3500 | 3500
10 | Installing fully restricted fencing at every construction site with marking tape (Using optimum-grade polyethylene, these tapes are manufactured and are demanded for civil, construction work warning text and symbols of safety. Additionally, these tapes are available in different colors, languages, designs and sizes) for construction site with clearly written warning notices for adjacent communities, as well as clearly marking at entry/ exit gates for workers as per Engineer-in-charge. (To be continued for total constrution period). | LS | 1 | 20000 | 20000
11 | Wastes disposal facility during the construction period; collection, transportation and disposing wastes in/c providing separate bin for organic & inorganic waste (To be continued for total constrution period). | LS | 1 | 15000 | 15000
| Total Amount, BDT |  |  |  | 543500

## Details of Cost Reduction (hidden)
Cost Reduction Details
Item No | Description of Items | Previous Amount in BDT | Revised Amount in BDT | % of Cost Reduction | Remarks
Part A | Production Tubewell (PTW) at Potibunia | 3835576.585 | 3835576.585 | 0%
Sub-Total of Part A |  | 3835576.585 | 3835576.585 | 0%
Part B | Civil Works
Part B1 | Pump House Building at Potibunia
| Concrete stairs have been replaced by prefabricated M.S ladder. On the first floor, cantilever portion has been omitted. Side wall has been replaced by MS railing at 1.0 meter height. At the roof, solar provision for internal use and the space for O&M works have been reduced; the floor area has been re-adjusted accordingly | 4795484.1528 | 3875363.8806 | 19.19% | Adapting a pump house building to a simplified structure tailored to the local context.
The other part of the pump house building are remaining same
Part B2 | Site Master Plan at Potibunia
| Boundary wall has been replaced by simple fencing with necessary columns | 814867.02 | 47276.24 | 94.2% | Contemplating the implementation of a straightforward fencing solution instead of a substantial boundary wall.
| The other parts are remaining same | 520099.6431 | 520099.6454 | -4.423e-07%
Part B3 | Tank Site at Camp 16 Block A (With Site Protection Works) | 495913.9401 | 495913.9401 | 0%
Part B4 | Tank Site at Camp 16 Block C | 569549.3806 | 569549.3806 | 0%
Sub-Total of Part B |  | 7195914.1366 | 5508203.0867 | 23.45%
Part C | Electro-mechanical Works
Part C1 | Mechanical Works (Submersible and Chlorine Pump with Accessories) | 900852 | 900852 | 0%
Part C2 | Solar System Works (Main Energy Source) | 2300313.04 | 2300313.04 | 0%
Part C3 | Electrical Works | 310823 | 310823 | 0%
Part C4 | Transformer for Electricity Network Connection (Backup Energy Source) | 541739 | 541739 | 0%
Part C5 | Generator (Optional Energy Source) | 1016467 |  | 100% | The primary energy source is envisioned to be a solar system, with the electricity network serving as a backup energy source.
Sub-Total of Part C |  | 5070194.04 | 4053727.04 | 20.05%
Part D | Water Networks, House Connections & Tap Stands and Water Tanks
Part D1 | Water Network, HDPE PN 8, SDR 21 (with Valves and Chambers)
D1.1 | Water Distribution Network at Potibunia | 4147101.5591 | 1509065.251 | 63.61% | The previous cost was determined using standard practices for PN10 HDPE pipe and considering in molded fittings. However, the rate has been revised to align with local practices, PN 8 HDPE pipes and adhere to the guidance provided by UNICEF. Additionally, the diameter has been modified from 160mm to 125mm for transmission main and distributon main of Potibunia host community.
D1.2 | Water Distribution Network at Camp 16 Block A | 1651195.7408 | 2232497.8745 | -35.2%
D1.3 | Water Distribution Network at Camp 16 Block C | 1034306.3515 | 52801.2851 | 94.9%
D1.4 | Water Transmission Network from PTW to Camp 16 Block A&C | 3404175.0699 |  | 100%
Sub-Total of Part D1 |  | 10236778.7213 | 3794364.4105 | 62.93%
Part D2 | House Connection and Tap Stand with Water Meter
D2.1 | House Connection with Water Meter at Potibunia Host Community (126 Nos.) | 3749813.68 |  | 100% | A basic water meter chamber has been incorporated as an essential component of the house connection tap stand, consolidating it rather than having a separate chamber. Additionally, a single tap has been chosen instead of two for each house connection, with the aim of streamlining costs..
D2.2 | Tap Stand with Water Meter at Camp 16 Block A&C (30 Nos.) | 964215.9587 | 673972.3135 | 30.1% | A simple water meter chamber has been considered as an integral part of tap stand, instead of separate chamber.
Sub-Total of Part D2 |  | 4714029.6387 | 673972.3135 | 85.7%
Part D3 | Water Tank with Piping & Valve Arrangement (Potibunia and Camp 16 Block A&C)
D3.1 | Food Graded Plastic Overhead Water Reservoir | 937232 | 937232 | 0%
D3.2 | Piping & Valve Arrangement at Water Tank Site | 550573 | 398780 | 27.57% | PN 8 pipes have been chosen for required lengths instead of PN 10. 50mm HDPE ball valve is now chosen for the water tank drainage system, replacing the Brass Gate Valve for the cost reduction purpose.
Sub-Total of Part D3 |  | 1487805 | 1336012 | 10.2%
Part E | Others
Part E1 | ESMP | 180664 | 180664 | 0%
Part E2 | O&M | 474800 |  | 100% | May consider with O&M cost of the project, instead of Capital Cost
Part E3 | Office Furniture | 105000 |  | 100% | May consider with O&M cost of the project, instead of Capital Cost
Part E4 | Insurance | 336462.0375 |  | 100%
Sub-Total of Part E |  | 1096926.0375 | 180664 | 83.53%
Grand-Total (Summation of Sub-Total of Part A, B, C, D and E) |  | 33637224.1591 | 19382519.4358 | 42.38% | Total Cost Reduction: 89,73,540.16 BDT
Total Cost Reduction: 14254704.72 BDT