## Summary
NGO Forum for Public Health Project Name: Sustainable WASH Solution in Cox's Bazar Technical Specification for Water Distribution Networks (WDN) on Whykong union, Teknaf, Cox's Bazar Site Location: In various places within Whykong Union, Teknaf Upazila, Cox's Bazar Distric
Date: 12.08 2025
TECHNICAL SPECIFICATION ( Summary)
Sl NO: | Specification | Unit | Quantity | Unit Price(BDT) | Amount (BDT)
1 | Reservoir Structure & Sonar Panel Structure | Nos | 1
2 | Tap Stand | Nos | 12
3 | Solar Panel Materials Work | Nos | 1
4 | Pipe & fitting | Nos | 1
5 | Water Source Devel.(Borehole) | Nos | 1
6 | Tool Box | Nos | 1
0
Inword:
Prepare By:-
Mohammad Noor
Public Health Engineer
Sustainable WASH Solution Project
NGO Forum For Public Haalth

## Structure Work
NGO Forum for Public Health Project Name: Sustainable WASH Solution in Cox's Bazar Technical Specification for Water Distribution Networks (WDN) on Whykong union, Teknaf, Cox's Bazar BoQ of Structure for 10 K water network Reservoir Site Location: In various places within Whykong Union, Teknaf Upazila, Cox's Bazar District
TECHNICAL SPECIFICATION ( BoQ for WDN )
BoQ of Structure for 10 K water network Reservoir
SL | Description | Unit | Quantity | Unit Price | Amount
A.1 | Site preparation work including earth excavation and filling, breaking and removing of old subsatnace carrying and disposing of old unusable materials to a safe distance and including arranging for and supplying all necessary tools and equipment at work site etc. All complete according to the instruction of NGOF/EIC. | L.S | 1
A.2 | Earth Work Excavation: Earth Work Excavation for platform by manually excavating earth to the lines, grades and elevation as per the drawing & design. All complete according to the instruction of NGOF/EIC. | Cft | 864
A.3 | Earth Filling: Sand filling in foundation trenches and plinth with fine local sand having minimum fineness modulus (FM) of .50 in 150mm/75 mm layers, leveling, watering and consolidating each layer by layer up to finished level, etc. All filling completed as per direction of engineer-in-charge and as per drawing and design | Cft | 70
A.4 | Single Layer Brick Flat Soling: Single layer brick flat soling with first class brick at the base of the platform, including carrying bricks, filling the interstices tightly with sand of minimum (FM 1.50), watering, leveling, dressing etc. All complete according to the instruction of NGOF/EIC. | Sft | 170
A.5 | Cement Concrete work (C.C) in the platform with Portland cement, best quality coarse sand (50% quantity of sand minimum F.M. 1.2 and 50% quantity of coarse sand of minimum F.M. 2.5) and stone chips 20mm down graded, in/c mixing appropriately, casting, laying, compacting and curing for the requisite period. The mixture proportion of cement sand and aggregate should be 1:3:6. All complete according to the instruction of NGOF/EIC. | Cft | 58
A.6 | Reinforcement Cement concrete work (RCC) in the platform with Portland cement, best quality coarse sand (50% quantity of sand minimum F.M. 1.2 and 50% quantity of coarse sand of minimum F.M. 2.5) and stone chips 20mm down graded, in/c mixing appropriately, casting, laying, compacting and curing for the requisite period. The mixture proportion of cement sand and aggregate should be 1:1.5:3. All complete according to the instruction of NGOF/EIC. | Cft | 370
A.7 | High strength MS deformed bar( grade 60/72, 500W) supply, fitting & fixing such as fabrication, jointing, cutting,binding etc. all complete as per direction of EIC | Kg | 1490
A.8 | 250 mm brick work with 1st class bricks in cement moter(1:4) and making bond with connected wall.. | Cft | 59.76
A.9 | 125 mm brick work with 1st class bricks in cement moter(1:4) and making bond with connected wall.. | Sft | 36
A.10 | Plaster work (with NCF): Minimum 12mm thick cement plaster (1:4) including washing of sand ( F.M of sand:1.2), cleaning of wall surface, curing for requisite period. All complete according to the instruction of NGOF/EIC. | Sft | 888.75
A.11 | Weather coat paint of approved best quality and colour delivered from authorized local agent of the manufacturer in a sealed container, applying to wall in two coats over a coat of brand specified primer or sealer elapsing specified time for drying/recoating including cleaning drying, making free from dirt, grease, wax, removing all chalked & scaled materials, fungus, mending good the surface defects, sand papering the surface and necessary scaffolding, spreading by brush/ roller/spray etc. all complete as per direction of the engineer-in-charge. | Sft | 888.75
A.12 | Supply fitting & fixing of 38mm GI pipe railing with cement bond a good quality parallel continous steel hand railing in the floor and selected S.S Pipe and good welding on two layer handrail connected 3.5 feet height.First layer (Horizontal bar) S.S bar will 1.5" (Inch) dia and 2nd layer.(Horizontal bar) SS bar will 1.5" (Inch) dia and 3rd layer also 1.5" (Inch) dia. SS pipe post should be install 3 feet C/C with and good welding and C.C casting (6"X6"X6") which necessary equipments accepted by Engineer.all complete as per direction of EIC | Rft | 217
| Supply fitting & fixing of 4 nos 50 mm GI pipe Posting/Column Base plate with good quality welding for 2 nos and other 2 nos R.C.C custing in column which necessary equipments accepted by Engineer.all complete as per direction of EIC | Rft | 40
A.13 | Supply fitting & fixing of 38mmX38mmX5mm MS Angle Stair all complete as per direction of EIC. | Kg | 78
| Supply fitting & fixing of MS angle Rafter will be placed 4 Nos for fixing the roof and will be placed along Purling rafter parallel and good quality welding must be acceptable. All complete will beaccepted by the Engineer-in-charge. Angle size 38mm (1.5") X 38mm (1.5") X 5mm and 4650 mm (15'-6") long | Kg | 65
| Supply fitting & fixing of MS angle Purlin will be placed 4 Nos for fixing the roof and will be placed along rafter parallel and good quality welding must be acceptable. All complete will beaccepted by the Engineer-in-charge. Angle size 38mm (1.5") X 38mm (1.5") X 5mm and 3480 mm (11'-6") long | Kg | 48
A.14 | Supply, fitting & fixing of 18"X24" Stone Plate Visibility all complete as per direction of EIC | Nos | 1
A.15 | Paint:lnterior standard acrylic emulsion paint (plastic, Enamel, weather or matt finish) of approved best quality and color delivered from authorized local agent of the manufacturer in a sealed container; applying to interior wall and ceiling with surface preparation including cleaning drying, making free from dirt, grease, wax, removing all chalked and scaled materials, fungus, mending good the surface defects using sand paper and necessary scaffolding; applying necessary interior sealer of specified brand on prepared surface; then applying necessary interior putty of specified brand for leveling, spot filling, crack filling and cutting by sand paper/zero water paper; finally applying 2 coats of emulsion paint spreading by brush/roller/spray & necessary scaffolding elc. up to desired finishing, elapsing specified time for drying or recoating; all complete in all floors and accepted by the Engineer-in-charge. | Sft | 888.75
Grand Total Amount including VAT & TAX= |  |  |  |  | 0
Inward:
Note: All type of work will be included Transportation, Fitting fixing , Vat & Tax. Above all measurement/quantity will be more or less. And site list will be change as per local context & as per govt. decision.
Prepare By:-
Mohammad Noor
Public Health Engineer
Sustainable WASH Solution Project
NGO Forum For Public Haalth

## Tap Stand
NGO Forum for Public Health Project Name: Sustainable WASH Solution in Cox's Bazar Technical Specification for Water Distribution Networks (WDN) on Whykong union, Teknaf, Cox's Bazar BoQ of Tap Stand Site Location: In various places within Whykong Union, Teknaf Upazila, Cox's Bazar District
TECHNICAL SPECIFICATION ( BoQ for WDN )
BoQ of Tap Stand
Sl. No. | Description of Items | Unit | Quantity | Unit Price | Total Amount
B.1 | Earth Work Excavation for platform by manually excavating earth to the lines, grades and elevation as per the drawing & design. All complete according to the instruction of NGOF/EIC. | Cft | 50.625
B.2 | Earth Filling: Earth filling in the trench with sand (minimum F.M. 1.20) in desire layers in/c leveling, watering and consolidating each layer up to finished level etc. Dry density after compaction shall not be less than 95% of MDD. All complete according to the instruction of NGOF/EIC. | Sft | 15.625
B.3 | Polythene Sheet Earth supplying filing and ground level make flat compacting and preparing base at Martyrs Monuments compund for ramp. Should be compacting soil by using water and durmujing. | Sft | 31.25
B.4 | Single Layer Brick Flat Soling: Single layer brick flat soling with first class brick at the base of the platform, including carrying bricks, filling the interstices tightly with sand of minimum (FM 1.50), watering, leveling, dressing etc. All complete according to the instruction of NGOF/EIC. | Sft | 21.66
B.5 | 4" Cement concrete work (CC) in the platform with Portland cement, best quality coarse sand (50% quantity of sand minimum F.M. 1.2 and 50% quantity of coarse sand of minimum F.M. 2.5) and stone chips 20mm down graded, in/c mixing appropriately, casting, laying, compacting and curing for the requisite period. The mixture proportion of cement sand and aggregate should be 1:3:6. All complete according to the instruction of NGOF/EIC. | Cft | 7.2
B.6 | Brick work: 10"& 5" brick wall with first class bricks and cement morter (1:4) and making bond with protection wall and properly raking out of Joints between bricks, including necessary cleaning and soaking the bricks for at least 24 hours before use and screening, curing at least for 7 days and other necessary charges. All work complete as per design and instruction of Engineer in-charge. (6'-3"-0"X5'-0"X1'-3") | Cft | 22.71
B.7 | Minimum 12mm thick cement plaster & net cement finishing (1:4) with neat cement finishing in the exposed surface of the wall (inner side and bottom side) all complete as per direction of the /EIC (Minimum F.M of sand:1:2) | Sft | 36
B.8 | Supplying,fitting and fixing 12" x 10" , visibility stone plate/ tiles with massage as per specification. All complete according to the instruction of NGOF/EIC (Material Thickness: 19mm stone plate, Printing: Stone print) | Each | 1
B.9 | Supply, fitting & fixing of water collection tape and drain system
| GI 1½" socket | pcs | 2
| GI 1" socket | pcs | 2
| GI Elbow 1" | pcs | 3
| GI pipe 1" dia | rft | 3.5
| GI tee 1" dia | pcs | 4
| GI S-Nipple 1" | pcs | 2
| GI S-Nipple ¾" | pcs | 2
| GI Tee ¾" | pcs | 3
| GI Reducing socket ¾" x ½" | pcs | 2
| GI End cap 1" | pcs | 1
| Globe valve brass ¾" | pcs | 1
| Handle SS Bibcock with high quality | pcs | 2
| Thread tape | pcs | 4
Sub- Total Amount including VAT & TAX
For 10 tap stand |  | Nos | 10 | 0
Grand Total-Amount including VAT & TAX=
Inward:
Note: All type of work will be included Transportation, Fitting fixing , Vat & Tax. Above all measurement/quantity will be more or less. And site list will be change as per local context & as per govt. decision.
Prepare By:-
Mohammad Noor
\ | Public Health Engineer
Sustainable WASH Solution Project
NGO Forum For Public Haalth

## Solar Panel Work
NGO Forum for Public Health Project Name: Sustainable WASH Solution in Cox's Bazar Technical Specification for Water Distribution Networks (WDN) on Whykong union, Teknaf, Cox's Bazar BoQ for Solar Panel Materials Site Location: In various places within Whykong Union, Teknaf Upazila, Cox's Bazar District
TECHNICAL SPECIFICATION ( BoQ for WDN )
BoQ for Solar Panel Materials
Work -2
Sl # | Description of item/work | Specification | Required Brand | Qty | Unit | Unit Price | Total Price
D.1 | Solar PV-Module | Capacity: 550Wp, Half-Cell, Mono Warranty: 25 Years | OSDA | 6 | Pcs
D.3 | Submersible Pump with Pump Controllar | Item code: 868248, Brand: RFL/GAZI Water Pump Model: 100QRm16/06-XL, Type: Water pump Well inch: 4" , Dn. inch: 2" , Color: Silver & blue (As given picture)., Power HP: 2 , KW: 1.5 , Capacity, Head (m): 15~18~35 , Flow Q-I/m: 350~300~50. Warranty: 2 Years:- 1. Coil burning & Spare will be free for 1st year along with service 2. Only service will be free for 2nd year | RFL/GAZI | 1 | Pcs
D.4 | Float Switch | Float Switch for Water Tank | Pedrolla/RFL/GAZI | 1 | Set
D.5 | PV Disconnect/Magnetic Conductor | DC1200V 40A PV DC Disconnect Switch IP66 Waterproof 4P DC Isolator Switch Fo LLI | Super Star | 1 | Set
D.6 | PP2000 AC Power Pack | AC/DC Converter PP2000 AC Power Pack | Super Star | 1 | Set
D.7 | Submersible Cable | Submersible Cable: 3*4rm | SQ | 60 | M
D.8 | SS Wire Rope | 4mm with SS Clump: 10 Pcs | Reputed | 80 | M
D.9 | Cable and Accessories | Cable 2x1.3rm (Float Switch & Well Prove Sensor) | Reputed | 100 | M
|  | Upvc pipe 1.5 Inch | Reputed | 150 | Feet
|  | PVC Socket 1.5 Inch | Reputed | 15 | Pcs
|  | PVC Elbow | Reputed | 10 | Pcs
|  | GI Union | Reputed | 2 | Pcs
|  | GI -T (1.5/1/2) | Reputed | 1 | Pc
|  | Flange, Nut Bolt, Base Plat, Malty Socket, PVC Pipe and Clam | Reputed | 1 | Lot
D.10 | Lead Acid Battery | Capacity: 130Ah Warranty: 2 Years | Super Star Solar | 1 | Pc
D.11 | Dosing Pump (For Dosing Pump) | Model : TPG800NHP0800 Liquid : Acid/Chemical, Dosing Head : PVDF Suction, Discharge : PPE (10mm), Diaphragm Material : EPDM, Sp. Gravity : 1 kg/dm3, Temperature : Ambient Discharge Capacity : 7-18 LPH, Total dynamic head : 16-1 Bar, Drive Motor : 40 W Standardization : ISO 9001, 2008, Valve Ball Material : Alumina Ceramic O-ring : FKM / EPDM Seal & Gasket : EPDM / FPM Brand : SEKO Origin : Italy H] Pressure Bar: 1-16 Bar Warranty: 1 Year | SEKO/Super Star | 1 | Set
D.12 | Flow Meter (Pulse Type) (For Dosing Pump) | Flow Meter Model: K65-EM3R3PS Medium: Water Standard measure temperature: 20~80 Liner material: PTFE, Electrode material: SS 316L, Body & Flange: Carbon steel Flange type: ANSI150#, Coil material: Copper, Installation: Separate display Output Signal: 4-20mA, Pulse, RS485 Power supply: 220VAC, Normal pressure: 1.6Mpa, Protection Class: IP68, Display: Local flow rate, Total, Flow velocity, Brand: Koncept, Origin: Italy | Lorentz/Super Star | 1 | Pc
D.13 | Delivery | Material Transportation Cost up to Cox's Bazar | Job | 1 | Job
D.14 | Installation | Installation Cost | Job | 1 | Job
Sub-total (Including VAT & TAX)= | [6 empty] | 0
In Words :
Note: All type of work will be included Transportation, Fitting fixing , Vat & Tax. Above all measurement/quantity will be more or less. And site list will be change as per local context & as per govt. decision.
Prepare By:-
Mohammad Noor
Public Health Engineer
Sustainable WASH Solution Project
NGO Forum For Public Haalth

## Pipe & fittings
NGO Forum for Public Health Project Name: Sustainable WASH Solution in Cox's Bazar Technical Specification for Water Distribution Networks (WDN) on Whykong union, Teknaf, Cox's Bazar Bill of Quantities for Pipe Fitting Site Location: In various places within Whykong Union, Teknaf Upazila, Cox's Bazar District.
TECHNICAL SPECIFICATION ( BoQ for WDN )
BoQ of Tank & Pipe & fitting Work
SL | Description | Unit | Quantity | Unit Price | Amount
Pipe Networks
E.1 | 10000 Liter Water Tank (Standard quality) with Fittings & fixing of pipe networking as per the design. all complete to the direction of EIC. | Nos | 1
E.2 | Earth Work Excavation: Excavation and pipe laying, fitting & fixing of pipe networking as per the design. all complete to the direction of EIC (2000'-0" X 1'-6"X 3'-0") | Cft | 9000
E.3 | Earth Filling: Sand filling in foundation trenches and plinth with fine local sand having minimum fineness modulus (FM) of .50 in 150mm/75 mm layers, leveling, watering and consolidating each layer by layer up to finished level, etc. All filling completed as per direction of engineer-in-charge and as per drawing and design (2000'-0" X 1'-0" X 0'-6") | Cft | 1000
E.4 | Plumbing work: Carrying, fitting, fixing of required plumbing materials such as: HDPE pipe includings necessary fittings.
| 1) HDPE Pipe 110mm,(8.1 mm),PE-100, PN-12.5 , L-6 , Item code 009.101.256 meter with necessary fittings & fixing. | Rft | 250
| 2)HDPE Pipe 90mm,(8.2mm), PE-100, PN-16 , L-6, Item code 009.101.492 meter with necessary fittings & fixing. | Rft | 450
| 3) HDPE Pipe 63mm,(3.00mm), PE-100, PN-8 , L-6, Item code 009.101.437 meter winecessary fittings & fixing. | Rft | 800
| 4) HDPE Pipe 50mm,(2.4mm), PE-100, PN-8 , L-300 RfT, Item code 009.101.233 with necessary fittings & fixing. | Rft | 250
| 5) HDPE Pipe 32mm,(2.00mm), PE-100, PN-10 , L-300 RfT, Item code 009.101.213 with necessary fittings & fixing. | Rft | 250
E.5 | Suply , fitting & fixing of 110 mm HDPE Gate valve ( Flange type) with MS angle & Plate cover ,all complete as per direction of EIC | Nos | 2
E.6 | Suply , fitting & fixing of 90 mm HDPE Gate valve ( Flange type) with MS angle & Plate cover ,all complete as per direction of EIC | Nos | 1
E.7 | Disinfect all pipe work | L.S | 1
E.8 | Supply , fittings & Fixing of Water Flow meter all completed as per direction of EIC | Nos | 1
E.9 | Supply , fittings & Fixing of Over Head tank Connection, inlet, outlet, washline work (Brand-Rfl, Gazi, and equivelent available in the market)
| 1) 110 mm dia gate valve ( Best quality available in market) | Nos | 2
| 2) 90mm dia gate valve ( Best quality available in market) | Nos | 2
| 3) 50mm dia GI pipe ( Best quality available in market) | rm | 8
| 4) 50mm dia Non Return Valve ( Best quality available in market) | Nos | 1
| 5) 50mm dia GI Elbo ( Best quality available in market) | Nos | 12
| 6) 50mm dia Socket ( Best quality available in market) | Nos | 4
| 7) 50mm dia gate valve ( Best quality available in market) | Nos | 2
E.8 | All kind of Pipe fitting and fixing (Standard quality) | Job | 1
Sub-total (Including VAT & TAX) = |  |  |  |  | 0
In ward:
Note: All type of work will be included Transportation, Fitting fixing , Vat & Tax. Above all measurement/quantity will be more or less. And site list will be change as per local context & as per govt. decision.
Prepare By:-
Mohammad Noor
Public Health Engineer
Sustainable WASH Solution Project
NGO Forum For Public Haalth

## Borehole
NGO Forum for Public Health
Project: Sustainable WASH Solution in Cox's Bazar
Bill of Quantities for Borehole
Site Location: Whykong Union, Teknaf Upazilla
Bill of Quantities (BOQ) of Borehole
SL No | Details Description/Specification | Qty | Units | Unit price | Total Price
A | Borehole
Site preparation & Boring work
1 | Mobilization: Mobilization of human resources, materials, equipments and boring tools at spot to accomplish the assignment as per design and direction of the Engineer-in-charges. Also ensure safety & security surrounding area. After completion the work site should have to clean. | 1 | LS |  | 0
2 | Boring by using jet method to 200mm or 8'' dia cutter for initial 600 feet depth and 38 mm dia GI pipe and other equipment capable of drilling up to a depth of 600 feet by water jet system and Final install 4"x1.5" dia well installation. protection of caving by supplying necessry casing pipe, withdrawal of boring pipes & casing pipes etc. Includings transportation of boring pipe, associated materials & equipment of boring and construction of derrick/ scaffold, dismantling the same, levelling, dressing, cleaning the site after completion of the works. Collection of soil sample of an interval of 3m in a transparent cellophane bag and done the installation.
2.1 | From 0 - 400 feet (using 200mm dia. Cutter) | 400 | Rft
2.2 | From 400 - 600 feet (using 200mm dia. Cutter) | 200 | Rft
2.3 | Sample Collection: Supply wooden sample collection tray and poly bag and monitor as per EIC instrction. | 1 | ls
3 | Fitting Fixing & Plumbing work: Carrying, fitting, fixing of required plumbing materials such as: submersible pump in place, uPVC pipe , filter and blind pipe having check valve at the end, requisite fittings and fixtures, seal tape, solvent cement etc.
3.1 | uPVC pipe (4 inch dia, 6.00 - 6.90mm wall thickness, white color/gray color, 20 feet long each, Class-D (RFL(Priority)/ National/ Aziz, equivalent brand best quality in thein market). | 280 | Rft
3.2 | uPVC Robo Filter/Strainer (4 inch dia, 6.0 mm to 6.90 mm wall thickness, 20 feet long each,class-D (RFL (proirity), National, Aziz, equivalent brand, best quality ). (note: the will be variable based on the potential aquifer) | 100 | Rft
3.4 | uPVC Sand Trap (4 inch dia, 2.50 mm - 2.70 mm wall thickness, 20 feet long each,Class-D (RFL, National, Aziz, equivalent brand, best quality ). | 20 | Rft
3.3 | uPVC Recuder Cap ( PVC Filter 4" X 1.5") Robo, 2.50mm - 3.00 mm wall thickness, 6.5 feet long each (RFL (priority), National, Aziz, equivalent brand, best quality) | 1 | Nos
3.5 | Solvent Cement/Gum tube wt. 500 gm (best quality/brand/konne japan). | 2 | Nos
3.6 | Bleaching powder (best quality/brand) | 1 | Kg
4 | Gravel Pack Filling_(Shrouding & Sealing of coarse sand (FM-2.50)
4.a | Gravel Pack/Sand Filling: Filling up of the space between bore hole & the tube well by coarse sand (minimum FM-2.5) from bottom of the sand trap to top of the filter up to 100 Feet (Total Out of pipe lowaring 400 feet) | 26 | cft
4.b | Second Case/Bentonite Seal: Filling up of the space from the top of the Sylther coarse sand up to 6m with the balls of 0.118-.196 mm dia or pellet which is made of bentonite power & local sand of 1:2 Bentonite power and local sand after completing 20 feet bentonite and then using the shylet as per direction EIC will be managed by the vendor (250Total Out of pipe lowaring 400 feet). | 64 | Cft
4.c | Sanitary Seal/ Clay Seal: The remaining bore hole spaces are filled with local Sand as per specification (50Total Out of pipe lowaring 400 feet). | 13 | Cft
5.1 | 1.25" inch Tread pipe with fitting and fixing | 250 | FT
5.2 | Pump Security box brick work (2'- 6"x 2'-6" size along with heihgt 2'-6" and covert slab RCC 3" (1:2:4) with plaster and net cement finishing work. All work completed as per direction of engineer-in-charge and as per drawing and design | 1 | Set
10 | Tube-well cleaning by air compressor: after drilling and lowering Tube-well must cleaning by air compressor untill water is clean and remove debris from the well. As per EIC instrction silt, sand and other accumulated materials that remove from the water flow. | 1 | ls
11 | Water Quality analysis (E-coli,Iron, Mn(Manganise),pH, Arsenic, Chloride, Hardness, Turbidy) at nearest DPHE laboratary , NGOF laboratary or any other recognized testing laboratory. | 1 | ls
Sub-Total (Including VAT & TAX) =
In ward:
Note: All type of work will be included Transportation, Fitting fixing , Vat & Tax. Above all measurement/quantity will be more or less. And site list will be change as per local context & as per govt. decision.
Prepare By:-
Mohammad Noor
Public Health Engineer
Sustainable WASH Solution Project
NGO Forum For Public Haalth

## Tool Box
NGO Forum for Public Health Project Name: Sustainable WASH Solution in Cox's Bazar Technical Specification for Water Distribution Networks (WDN) on Whykong union, Teknaf, Cox's Bazar BoQ for Tool Box System Site Location: In various places within Whykong Union, Teknaf Upazila, Cox's Bazar District
TECHNICAL SPECIFICATION ( BoQ for WDN )
BoQ for Tool Box System
Sl NO: | Supply and Installation Solar System and pump | Unit | Quantity | Rate | Total Taka
1 | Pipe range 18" (HMBR/TOOLSON/INTRACO) | Nos | 2
2 | Multi Players (HMBR/TOOLSON/INTRACO) | Nos | 1
3 | Pipe Thread Cutter Machine full Box (1/2'', 3/4'', 1'', 1.5'' & 2'' individual) (HMBR/TOOLSON/INTRACO) | Set | 1
4 | Star Sqru Driver 12" (HMBR/TOOLSON/INTRACO) | Nos | 1
5 | Flat Sqru Driver 12" (HMBR/TOOLSON/INTRACO) | Nos | 1
6 | Sly Range 12" (HMBR/TOOLSON/INTRACO) | Nos | 2
7 | seal tape/Putting M Sill | Nos | 12
8 | Tool box 20"X10"X8" Ms Sheet 20gag | Nos | 1
Sub Total (Including VAT & TAX) BDT |  |  |  |  | 0
In word :
Note: All type of work will be included Transportation, Fitting fixing , Vat & Tax. Above all measurement/quantity will be more or less. And site list will be change as per local context & as per govt. decision.
Prepare By:-
Mohammad Noor
Public Health Engineer
Sustainable WASH Solution Project
NGO Forum For Public Haalth