## Electrical Item for NFI at C1E
Lot 1 Electrical Bill of Quantities (BOQ) with Stock Items For NFI Distribution Point at Camp 1E, Ukhiya, Cox’s Bazar.
Item | Description (All the item must be supplied and installed as per TOR) | Unit of Measure | Quantity | Brands for reference only | Remarks | Reuired Minimum Warranty | Offered Warranty | Offered Brand Name | Specification Sheet/Brochure/Catalogue/Data sheet /Test certificate is submitted? (Bidder may submit one of the mentioned required document above) (Yes/No)
SECTION 1: Supply of Distribution Boards and Circuit breakers
1.1 | MDB of Camp 1E NFI Distribution Center
| Three Phase Metal Distribution Board iP66, high qaulity rust proof and electric insulation paint, 100% water tight seal, with gastgets, fitted with digital Voltmeter+ammeters+selector switch (ph-N&ph-ph), and three phase indicator light, plexi-glass screen over the busbars) All other accessories as per technical specification & drawings. Size: 30"x24"x8", Copper bar size : 13"x1.25"x5 mm (3 No's For 3 Phase) and 8"x1.25"x 5mm (2 Nos For Neutral and Earthing) Maintain All Colour Code With Heatshrink Tube and Busbar Each Hole Distance Min 1.5" Mounted on insulator at both ends. Capacity : 200-300A Customize For : (Incoming - 1 TP MCCB, Outgoing- 5 DP MCB approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 32 A TP MCCB, 400 V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 32 A DP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 20 A DP MCB, 220 V, 10 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.2 | DB 1: (Guard Room, EPR Room, Generator Room, Breast Feeding Room)
| 12 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 20A, DP MCB, 220V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.3 | DB 2: Office Rooms
| 10 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 20A, DP MCB, 220V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.4 | DB 3 : Waiting shade 1 (Male & Female)
| 12 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 32 A, DP MCB, 220V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 4 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 4 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.5 | Three Phase AC Combiner Box: Three Phase (R,Y,B) and N+PE (Neutrul and Protection Earthing) Busbar Arrangement. Box Size: 18"x14"x8" Copper Busbar Busbar Thickness 5mm and shall be of suitable dimensions so as to accommodate the circuit breakers and busbars with insulated shroud with sufficient spacing including internal connection cables in the board and other materials, shall have hinged type door locks, circuit directory shall be suitable for concealed /surface mounted type having PVC cable glands/grommets of appropriate sizes, shall have knockout for conduits entry & exist, a suitable size copper plate earthing block must be provided inside the box. Customized for One Incoming TP MCCB and TP MCB For REB/PDB Incoming Circuit Breaker | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
1.6 | 32 A, TP MCCB, 400V, 10 KA for (REB/PDB Incoming Circuit Breaker) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
Total For Distribution Boards and Circuit breakers
SECTION 2: Supply of Cabling
2.1 | Single wire 1.5 sqmm RED Cu/PVC, (BYA) | Roll | 13 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.2 | Single wire 1.5 sqmm Black Cu/PVC, (BYA) | Roll | 10 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.3 | Single wire 2.5 sqmm RED Cu/PVC, (BYA) | Roll | 4 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.4 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 4 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.5 | Single wire 4 sqmm RED Cu/PVC, (BYA) | Roll | 3 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.6 | Single wire 4 sqmm Black Cu/PVC, (BYA) | Roll | 3 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.7 | Single wire 4 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 4 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.8 | 1x2C-4sqmm NYY | Meter | 40 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.9 | 1x2C-6sqmm NYY | Meter | 65 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.10 | 1x4C-6sqmm NYY | Meter | 45 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.11 | Single wire 6 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 2 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.12 | Single wire 16 sqmm Green Earthing Cu/PVC, (BYA) | Meter | 50 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
Total For Cabling
SECTION 3: Supply of Piping & Conduits
3.1 | 1 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 600 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.2 | 1 inch PVC Joined Bend | Pcs | 48 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.3 | 1 inch PVC Joined Socket | Pcs | 72 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.4 | 1 inch PVC T-Joint | Pcs | 60 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.5 | 1 inch PVC Elbow | Pcs | 60 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.6 | 1 inch PVC 4-Way Circular Box | Pcs | 36 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.7 | 1 inch PVC 3-Way Circular Box | Pcs | 36 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.8 | 1 inch PVC 2-Way Circular Box | Pcs | 36 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.9 | PVC Seal Joined Gum | Liter | 3 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.10 | 1.5 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 50 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.11 | 1.5 inch PVC Joined Socket | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.12 | 1.5 inch PVC Joined Bend | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.13 | 1.5 inch Joined Elbow | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.14 | PVC conduit 16x25 | Meter | 500 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.15 | PVC conduit 25x40 | Meter | 50 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.16 | PVC Flexible Pipe (Inside with steel)(Black) ; 0.5 Inch | Meter | 100 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | N/A
3.17 | PVC Flexible Pipe (Inside with steel)(Black) ; 1 Inch | Meter | 100 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | N/A
3.18 | PVC Flexible Pipe (Inside with steel)(Black) ; 1.5 Inch | Meter | 200 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | N/A
3.19 | Steel Saddle Clamp For Hose Pipe 0.5 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | N/A
3.20 | Steel Saddle Clamp For Hose Pipe 1 inch | Pcs | 24 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | N/A
3.21 | Steel Saddle Clamp For Hose Pipe 1.5 inch | Pcs | 24 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | N/A
Total For Piping & Conduits
SECTION 4: Supply of Lights, Sockets, and Light Switches
4.1 | Socket (universal type, multi-input, full set with back box) | Pcs | 19 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.2 | Socket (up to 20Amp)(three pin, for AC/Pump, full set with back box) | Pcs | 1 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.3 | LED Batten light full set (3500-5000K, cool white color, minimum 100lm/w, 1.5meter max lenght) max 40 Watt | Pcs | 41 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.4 | LED light bulb (cool white color, E27 screw, min. 100lm/w )/ 12 Watt | Pcs | 22 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.5 | LED light bulb base (plastic, internal use, E27 screw, ) | Pcs | 22 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.6 | LED flood lights (heavy-duty structure, iP65, efficient heat dissipation, operating voltage (200 to 250 V), A+ energy saving, bright white light colour, minimum of 120Lm/W) ; 30 Watt | Pcs | 17 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.7 | Light Switches - one way, 1 Gang, min. 6 amp,(full set with back-box) | Pcs | 8 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.8 | Light Switches - one way, 2 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.9 | Light Switches - one way, 3 Gang, min. 6 amp,(full set with back-box) | Pcs | 12 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.10 | Light Switches - one way, 4 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
Total For Sockets and Light
SECTION 5: Supply of Fans
5.1 | Ceiling Mounted Fan (Open Type, 56 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 23 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.2 | Ceiling Mounted Fan (Open Type, 36 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 2 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.3 | Wall-Mountain Fan (Caged Type, 18 inch heavy duty, all plastic, up to 32 inch diameter, full set, equipped with speed controler and On/Off switch) | Pcs | 2 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.4 | Fans Speed Controller (rated up to 10 amp, full set with back box) | Pcs | 25 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.5 | Ventilation Fans (plastic type, mute, water proof configration); 12 Inch | Pcs | 6 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
Total For Fans
SECTION 6: Supply of Miscellaneous Items
6.1 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Red | Pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.2 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Yellow | pcs | 12 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.3 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Blue | pcs | 12 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.4 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Green | pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.5 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Black | pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.6 | Plastic rowel plug no.10 | Pcs | 3000 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.7 | 1 Inch twin thread cross-head wood screws suitable for plastic plug no.10 | Pcs | 3000 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.8 | PIB Tape (Black) | Pcs | 15 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.9 | Cable tie 200 mm | Pkt | 5 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.10 | Cable tie 300 mm | Pkt | 12 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.11 | S-shaped fan hooks made of 12mm rod, complete with fixing on angle by welding (including enamel painting on a corrosion resistive primer coat of red oxide) Size: As Per Site Measurment | Pcs | 25 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | N/A
6.12 | 2x2 inch Steel Angle Beam (L-shaped) for the ceiling fans installation on the roof beams, complete with weliding enamel painting on a corrosion resistive primer coat of red oxide. | Meter | 100 | BSRM, KSRM, and GPH., or Equivalent Brand. |  | N/A
6.13 | Buried Cable Warning Sign on 8”X8” Silver sheet with Plastic Paint | Nos | 4 | BSRM, KSRM, and GPH., or Equivalent Brand. |  | N/A
6.14 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6 rm RED | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | N/A
6.15 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Yellow | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | N/A
6.16 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Blue | Pcs | 12 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | N/A
6.17 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Black | Pcs | 12 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | N/A
6.18 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Green | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | N/A
6.19 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 10 rm | Pcs | 48 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | N/A
6.20 | 10mm SS Royal Bolt | Nos | 18 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | N/A
6.21 | Silicone Gum | Nos | 5 | Sambond, V-tech and Oci , or Equivalent Brand. |  | N/A
6.22 | No. Tag (0-9); Every Digit | Packet | 1 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | N/A
Total For Miscellaneous Items
SECTION 7: Supply of Earthing & Lightening Items
7.1 | 20 feet long, 40mm dia, 2.35 mm thickness GI Pipe, threaded both end (with 10mm thorough holes at every 500mm interval and every alternate hole 90 degree apart in direction) | Pcs | 9 | Brand for reference only: RFL Falcon, SIMEX, HATIM, GBTL, Steel Mark Ltd, or Equivalent Brand. |  | 12 Month
7.2 | Copper MGB ( 14" x3" x 1/4" ) with accessories | Pcs | 4 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.3 | Air terminals 2 feet long, 12.7mm dia, Copper. | Pcs | 13 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.4 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper | Pcs | 13 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.5 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper ( Joint Socket ) | Pcs | 6 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand.
7.6 | Copper solid strip 20mm x 3mm (60 mm2) | Meter | 150 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.7 | Ruppen Screw (2 inch) | Pcs | 100 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.8 | Copper Tape Clip | Pcs | 100 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.9 | Inspection box with copper busbar (30mm x 5mm x 200mm) with 18 gauge steel sheet | Pcs | 5 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.10 | Insulator for installation of MGB | pcs | 8 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.11 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 60 ft long | Pcs | 3 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.12 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 40 ft long | Pcs | 6 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.13 | U-shaped clamp (Copper, used for cable-cable connection): 50 sqmm, min 190 amp | Pcs | 18 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.14 | Rubber 5mm thickness 2' x 2' | Pcs | 4 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.15 | 25mm2 cable shoe/lug to connect 2SWG ECC | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
Total For Supply of Earthing & Lightening Items
SECTION 8: Supply, Testing and Commissioning of Fire safety and Ditection Items
8.1 | Supply & fixing the following capacities multi purpose ABC dry chemical powder stored pressure type withmanometer system fire extinguisher suitable for repeated use complete with wall bracket, CO2 cartridge,easy refilling system etc. as per sample accepted & approved by the Engineer. Mono Amonium Phosphate based 40% ABC dry chemical agent & hasa moisture-proof, anti-caking properties. Working pressure : 12 BAR minimum & Test pressure : 25 BAR minimum. Proper fire rating (as per NFPA 10) according to the capacity of the extinguisher. Manufacturerer certificate shall have to be submitted if needed. Also sample of the dry chemical powder will be tested by the proper authority in Bangladesh if needed. Country of origin : CHINA / MALAYSIA or equivalent 5 Kg Capacity. | nos | 11 | Brand fpr reference only: Taifun, Sunrise, Hunter or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.2 | Supply & fixing the following capacities Carbon-di-Oxide type fire extinguisher suitable for repeated use complete with wall bracket, discharge nozzle etc. as per sample accepted & approved by the Engineer. Country of origin : CHINA / MALAYSIA or equivalent product. 5 Kg. capacity.. | nos | 11 | Brand fpr reference only: Taifun, Sunrise, Hunter or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.3 | Conventional fire alarm control panels : Supply and installation of 08 zone conventional fire alarm control panel with power supply unit, batteries and other accessories. The panel shall be complete with zone indicating LED, faultindication and optionaltelephone jack etc. The panel shall have input 220V AC and output 24V DC.Panel shall be confirmed UL listed / FM approvedapproved. Country of origin : AUSTRALIA / CANADA / JAPAN / USA / European countries or their licensed manufacturing units located globally. 08 zone capacity | Each | 1 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.4 | INITIATING DEVICES SMOKE DETECTOR ( CONVENTIONAL TYPE) Supply and installation of conventional smoke detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC. | Each | 4 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.5 | INITIATING DEVICES Heat Detector( CONVENTIONAL TYPE) Supply and installation of conventional heat detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC | Each | 1 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.6 | INITIATING DEVICES Manual call point ( CONVENTIONAL TYPE) Supply and installation of conventional type manual call point like break glass switch or single action pull station complete with back box and all other accessories and consumables. Power supply shall be 24V DC. It shall be UL listed / FM approved . | Each | 5 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.7 | Notification devices Strobe / horn with strobe Supply and installation of conventional type horn with strobe for notification purpose complete with back box, suitable to produce electronic sound level of 87 to 95 dBA @ 3 meter and illumination shall be not less than 75 candela red color shall be UL listed / FM approved . Power supply shall be 24VDC. | Each | 6 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.8 | SIGNALING CABLE WITH PVC CONDUIT & ACCESSORIES Surface conduit wiring with the following FPLR/ FPLP/ FPL type UL listed / FM Approved / LPCB Approved cable. PVC Insulation for each core shall be FR (Fire Rated) & Drain wire, shield (Aluminum Foil tape/ PET tape) shall meet the minimum requirement as per NEC (National Electric Code) or NFPA 70 or BS. Jacket shall be Fire Rated. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) . The work shall be carried out as per direction & approval of the Engineer in charge. 2C-1.5 sqmm (FPLR/ FPLP/ FPL ) cable with 1.5 sqmm (FR) ECC wire through PVC pipe of minimum inner dia 25 mm having wall thickness of 1.5 mm | Meter | 126 | Brand for reference only: Tianjie Indrustrial or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
Total for Supply, Testing and Commissioning of Fire safety and Ditection Items
SECTION 9: Supply of Construction Earthing Pit Items
9.1 | 1st Class Bricks | Nos | 1170 | Local Indrustries. |  | 12 Month
9.2 | 10mm Rebar | Kg | 63 | Brands for reference only: BSRM, KSRM, GPH or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.3 | Cement | Cft | 9 | Brands for reference only: Bashundhara Cement, Shah Cement, Crown Cement, Premier Cement, Fresh Cement or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.4 | Local Sand | Cft | 36 | Local Indrustries. |  | 12 Month
9.5 | Brick Chips | Cft | 36 | Local Indrustries. |  | 12 Month
Total For Construction Earthing Pit Items
NAME:
IN THE CAPACITY OF:
DULY AUTHORIZED TO SIGN BID FOR AND ON BEHALF OF:
DATE:
OFFICIAL STAMP:

## Electrical Item for Camp 4 PHC
Lot 2 Electrical Bill of Quantities (BOQ) with Stock Items For PHC Traning Center at Camp-4, Ukhiya, Cox's Bazar.
Item | Description (All the item must be supplied and installed as per TOR) | Unit of Measure | Quantity | Brands for reference only | Remarks | Reuired Minimum Warrenty | Offered Warranty | Offered Brand Name | Specification Sheet/Brochure/Catalogue/Data sheet /Test certificate is submitted? (Bidder may submit one of the mentioned required document above) (Yes/No)
SECTION 1: Supply of Distribution Boards and Circuit breakers
1.1 | MDB
| Three Phase Metal Distribution Board iP66, high qaulity rust proof and electric insulation paint, 100% water tight seal, with gastgets, fitted with digital Voltmeter+ammeters+selector switch (ph-N&ph-ph), and three phase indicator light, plexi-glass screen over the busbars) All other accessories as per technical specification & drawings. Size: 30"x24"x8", Copper bar size : 13"x1.25"x5 mm (3 No's For 3 Phase) and 8"x1.25"x 5mm (2 Nos For Neutral and Earthing) Maintain All Colour Code With Heatshrink Tube and Busbar Each Hole Distance Min 1.5" Mounted on insulator at both ends. Capacity : 200-300A Customize For : (Incoming - 1 TP MCCB, Outgoing- 1 TP MCCB and 2 DP MCB and 1 SP MCB approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 40 A, TP MCCB, 400V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 32 A, TP MCCB, 400V, 10 KA (Outgoing) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 32 A DP MCB, 230 V, 10 KA (Outgoing) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 20 A DP MCB, 230 V, 10 KA (Outgoing) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 230 V, 10 KA (Outgoing), | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.2 | SDB-1
| 12 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 32 A DP MCB, 220 V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 4 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.3 | SDB-2
| 10 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 20 A DP MCB, 230 V, 6 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 20 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.4 | SDB-3
| Three Phase 24 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 32 A, TP MCB, 400V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 20 A, SP MCB, 230V, 10 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 13 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 5 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.5 | Three Phase AC Combiner Box: Three Phase (R,Y,B) and N+PE (Neutrul and Protection Earthing) Busbar Arrangement. Box Size: 18"x14"x8" Copper Busbar Busbar Thickness 5mm and shall be of suitable dimensions so as to accommodate the circuit breakers and busbars with insulated shroud with sufficient spacing including internal connection cables in the board and other materials, shall have hinged type door locks, circuit directory shall be suitable for concealed /surface mounted type having PVC cable glands/grommets of appropriate sizes, shall have knockout for conduits entry & exist, a suitable size copper plate earthing block must be provided inside the box. Customized for One Incoming TP MCCB and TP MCB For REB/PDB Incoming Circuit Breaker | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
1.6 | 40 A, TP MCCB, 400V, 10 KA (REB/PDB Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
Total For Distribution Boards and Circuit breakers
SECTION 2: Supply of Cabling
2.1 | Single wire 1.5 sqmm RED Cu/PVC, (BYA) | Roll | 15 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.2 | Single wire 1.5 sqmm Black Cu/PVC, (BYA) | Roll | 13 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.3 | Single wire 2.5 sqmm RED Cu/PVC, (BYA) | Roll | 4 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.4 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 4 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.5 | Single wire 4 sqmm RED Cu/PVC, (BYA) | Roll | 5 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.6 | Single wire 4 sqmm Black Cu/PVC, (BYA) | Roll | 5 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.7 | Single wire 4 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 6 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.8 | 1x2C-4sqmm NYY | Meter | 40 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.9 | 1x2C-6sqmm NYY | Meter | 40 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.10 | 1x4C-6sqmm NYY | Meter | 60 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.11 | Single wire 6 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 1 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.12 | 1-4Cx10sqmm NYY | Meter | 50 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.13 | 1x10sqmm ECC Cu/PVC, (BYA) | Meter | 50 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
Total For Cabling
SECTION 3: Supply of Piping & Conduits
3.1 | 1 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 600 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.2 | 1 inch PVC Joined Bend | Pcs | 36 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.3 | 1 inch PVC Joined Elbow | Pcs | 36 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.4 | 1 inch PVC Joined Socket | Pcs | 36 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.5 | 1 inch PVC Joined T Socket | Pcs | 36 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.6 | 1 inch PVC 2-Way Circular Box | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.7 | 1 inch PVC 3-Way Circular Box | Pcs | 24 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.8 | 1 inch PVC 4-Way Circular Box | Pcs | 36 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.9 | PVC Seal Joined Gum | Liter | 3 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.10 | 1.5 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 40 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.11 | 1.5 inch PVC Joined Socket | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.12 | 1.5 inch PVC Joined Bend | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.13 | 1.5 inch Joined Elbow | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.14 | PVC conduit 16x25 | Meter | 600 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.15 | PVC conduit 25x40 | Meter | 50 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | 12 Month
3.16 | PVC Flexible Pipe (Inside with steel)(Black) ; 0.5 Inch | Meter | 100 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | 12 Month
3.17 | PVC Flexible Pipe (Inside with steel)(Black) ; 1 Inch | Meter | 100 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | 12 Month
3.18 | PVC Flexible Pipe (Inside with steel)(Black) ; 1.5 Inch | Meter | 100 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | 12 Month
3.19 | Steel Saddle Clamp For Hose Pipe 0.5 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | 12 Month
3.20 | Steel Saddle Clamp For Hose Pipe 1 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | 12 Month
3.21 | Steel Saddle Clamp For Hose Pipe 1.5 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | 12 Month
Total For Piping & Conduits
SECTION 4: Supply of Lights, Sockets, and Light Switches
4.1 | Socket (universal type, multi-input, full set with back box) | Pcs | 58 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.2 | Socket (up to 20Amp)(three pin, for AC/Pump, full set with back box) | Pcs | 3 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.3 | LED Light square shape full set (2000-3000K, warm white color, minimum 100lm/w, 600mmx600mm max dimensions)' 40 Watt | Pcs | 22 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.4 | LED Batten light full set ( 6500K, cool white color, minimum 100lm/w, 1.5meter max lenght) max 40 Watt | Pcs | 22 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.5 | LED light bulb (cool white color, E27 screw, min. 100lm/w )/ 12 Watt | Pcs | 21 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.6 | LED light bulb base (plastic, internal use, E27 screw, ) | Pcs | 21 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.7 | LED flood lights (heavy-duty structure, iP65, efficient heat dissipation, operating voltage (200 to 250 V), A+ energy saving, bright white light colour, minimum of 120Lm/W) ; 30 Watt | Pcs | 7 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.8 | Light Switches - one way, 1 Gang, min. 6 amp,(full set with back-box) | Pcs | 12 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.9 | Light Switches - one way, 2 Gang, min. 6 amp,(full set with back-box) | Pcs | 16 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.10 | Light Switches - one way, 3 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.11 | Light Switches - one way, 4 Gang, min. 6 amp,(full set with back-box) | Pcs | 18 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
Total For Sockets and Light
SECTION 5: Supply of Fans
5.1 | Ceiling Mounted Fan (Open Type, 56 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 20 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.2 | Ceiling Mounted Fan (Open Type, 36 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 2 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand.
5.3 | Fans Speed Controller (rated up to 10 amp, full set with back box) | Pcs | 24 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.4 | Ventilation Fans (plastic type, mute, water proof configration); 12 Inch | Pcs | 14 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
Total For Fans
SECTION 6: Supply of Miscellaneous Items
6.1 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Red | Pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.2 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Yellow | pcs | 12 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.3 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Blue | pcs | 12 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.4 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Green | pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.5 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Black | pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.6 | Plastic rowel plug no.10 | Pcs | 3000 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.7 | 1 Inch twin thread cross-head wood screws suitable for plastic plug no.10 | Pcs | 3000 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.8 | PIB Tape (Black) | Pcs | 15 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.9 | Cable tie 200 mm | Pkt | 5 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.10 | Cable tie 300 mm | Pkt | 15 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.11 | S-shaped fan hooks made of 12mm rod, complete with fixing on angle by welding (including enamel painting on a corrosion resistive primer coat of red oxide) Size: As Per Site Measurment | Pcs | 22 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
6.12 | 2x2 inch Steel Angle Beam (L-shaped) for the ceiling fans installation on the roof beams, complete with weliding enamel painting on a corrosion resistive primer coat of red oxide. | Meter | 50 | BSRM, KSRM, and GPH., or Equivalent Brand. |  | 12 Month
6.13 | Buried Cable Warning Sign on 8”X8” Silver sheet with Plastic Paint | Nos | 4 | BSRM, KSRM, and GPH., or Equivalent Brand. |  | 12 Month
6.14 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6 rm RED | Pcs | 48 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.15 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Yellow | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.16 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Blue | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.17 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Black | Pcs | 48 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.18 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Green | Pcs | 48 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.19 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 16 rm | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.20 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 25 rm | Pcs | 36 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.21 | 10mm SS Royal Bolt | Nos | 18 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.22 | Silicone Gum | Nos | 5 | Sambond, V-tech and Oci , or Equivalent Brand. |  | 12 Month
6.23 | No. Tag (0-9); Every Digit | Packet | 1 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
Total For Miscellaneous Items
SECTION 7: Supply of Earthing & Lightening Items
7.1 | 20 feet long, 40mm dia, 2.35 mm thickness GI Pipe, threaded both end (with 10mm thorough holes at every 500mm interval and every alternate hole 90 degree apart in direction) | Pcs | 8 | Brand for reference only: RFL Falcon, SIMEX, HATIM, GBTL, Steel Mark Ltd, or Equivalent Brand. |  | 12 Month
7.2 | Copper MGB ( 14" x3" x 1/4" ) with accessories | Pcs | 5 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.3 | Air terminals 2 feet long, 12.7mm dia, Copper. | Pcs | 9 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.4 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper | Pcs | 9 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.5 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper ( Joint Socket ) | Pcs | 5 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.6 | Copper solid strip 20mm x 3mm (60 mm2) | Meter | 70 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.7 | Ruppen Screw (2 inch) | Pcs | 100 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.8 | Copper Tape Clip | Pcs | 50 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.9 | Inspection box with copper busbar (30mm x 5mm x 200mm) with 18 gauge steel sheet | Pcs | 2 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.10 | Insulator for installation of MGB | pcs | 10 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.11 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 60 ft long | Pcs | 3 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.12 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 40 ft long | Pcs | 5 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.13 | U-shaped clamp (Copper, used for cable-cable connection): 50 sqmm, min 190 amp | Pcs | 16 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.14 | Rubber 5mm thickness 2' x 2' | Pcs | 5 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.15 | 25mm2 cable shoe/lug to connect 2SWG ECC | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
Total For Supply of Earthing & Lightening Items
SECTION 8: Supply and Installation of AC Item
8.1 | AC (Split type) Capacity: 24,000 BTU Energy Class : A++ Refrigerant: R410a Indoor Air Volume (m³/h): H-561/M-475/L-380 m³/h Inverter for Energy Saving Jet Cool & Heat Technology to drop temperature & heat up instantly Hidden LED display High density filter to remove more than 50% dust and other particles Cold-catalyst filter to remove formaldehyde and VOCs as harmful gases and odors Please Note: 1. The offer must include all necessary cables, ducts, pipes, and wires up to at least 15 feet to connect the indoor unit with the outdoor unit. The supplier should also provide a separate quote for each additional foot of cables, ducts, or pipes. 2. Equipment locations (indoor and outdoor units) must be agreed upon with a responsible person designated by UNHCR before installation. 3. The offer must include a robust, painted iron frame to hold and install the outdoor unit. Additionally, the supplier should provide a separate quote for a robust, painted iron security grill with a lock and key for the outdoor unit. 4.The power supply required for AC installation must be arranged independently by the vendors. 5. During the installation process of indoor and outdoor units, any drilling or screwing that causes damage to the structures must be repaired and restored to their original condition by the vendor. | Pcs | 2 | Brands for reference only: Gree, LG, Samsung, General, Media, Daikin, Hitachi, Panasonic, Mitsubishi Electric, TCL, Walton or equivalent, provided the offered air‑conditioning units meet the specified technical requirements, performance parameters, and applicable standards, and are acceptable to UNHCR. |  | 12 Month
Total For Supply of AC Items
SECTION 9: Supply, Testing and Commissioning of Fire safety and Ditection Items
9.1 | Supply & fixing the following capacities multi purpose ABC dry chemical powder stored pressure type withmanometer system fire extinguisher suitable for repeated use complete with wall bracket, CO2 cartridge,easy refilling system etc. as per sample accepted & approved by the Engineer. Mono Amonium Phosphate based 40% ABC dry chemical agent & hasa moisture-proof, anti-caking properties. Working pressure : 12 BAR minimum & Test pressure : 25 BAR minimum. Proper fire rating (as per NFPA 10) according to the capacity of the extinguisher. Manufacturerer certificate shall have to be submitted if needed. Also sample of the dry chemical powder will be tested by the proper authority in Bangladesh if needed. Country of origin : CHINA / MALAYSIA or equivalent 5 Kg Capacity. | nos | 11 | Brand fpr reference only: Taifun, Sunrise, Hunter or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.2 | Supply & fixing the following capacities Carbon-di-Oxide type fire extinguisher suitable for repeated use complete with wall bracket, discharge nozzle etc. as per sample accepted & approved by the Engineer. Country of origin : CHINA / MALAYSIA or equivalent product. 5 Kg. capacity.. | nos | 11 | Brand fpr reference only: Taifun, Sunrise, Hunter or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.3 | Conventional fire alarm control panels : Supply and installation of 08 zone conventional fire alarm control panel with power supply unit, batteries and other accessories. The panel shall be complete with zone indicating LED, faultindication and optionaltelephone jack etc. The panel shall have input 220V AC and output 24V DC.Panel shall be confirmed UL listed / FM approvedapproved. Country of origin : AUSTRALIA / CANADA / JAPAN / USA / European countries or their licensed manufacturing units located globally. 08 zone capacity | Each | 1 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.4 | INITIATING DEVICES SMOKE DETECTOR ( CONVENTIONAL TYPE) Supply and installation of conventional smoke detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC. | Each | 7 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.5 | INITIATING DEVICES Heat Detector( CONVENTIONAL TYPE) Supply and installation of conventional heat detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC | Each | 2 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.6 | INITIATING DEVICES Manual call point ( CONVENTIONAL TYPE) Supply and installation of conventional type manual call point like break glass switch or single action pull station complete with back box and all other accessories and consumables. Power supply shall be 24V DC. It shall be UL listed / FM approved . | Each | 11 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.7 | Notification devices Strobe / horn with strobe Supply and installation of conventional type horn with strobe for notification purpose complete with back box, suitable to produce electronic sound level of 87 to 95 dBA @ 3 meter and illumination shall be not less than 75 candela red color shall be UL listed / FM approved . Power supply shall be 24VDC. | Each | 13 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.8 | SIGNALING CABLE WITH PVC CONDUIT & ACCESSORIES Surface conduit wiring with the following FPLR/ FPLP/ FPL type UL listed / FM Approved / LPCB Approved cable. PVC Insulation for each core shall be FR (Fire Rated) & Drain wire, shield (Aluminum Foil tape/ PET tape) shall meet the minimum requirement as per NEC (National Electric Code) or NFPA 70 or BS. Jacket shall be Fire Rated. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) . The work shall be carried out as per direction & approval of the Engineer in charge. 2C-1.5 sqmm (FPLR/ FPLP/ FPL ) cable with 1.5 sqmm (FR) ECC wire through PVC pipe of minimum inner dia 25 mm having wall thickness of 1.5 mm | Meter | 209 | Brand for reference only: Tianjie Indrustrial or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
Total for Supply, Testing and Commissioning of Fire safety and Ditection Items
SECTION 10: Supply of Construction Earthing Pit Items
10.1 | 1st Class Bricks | Nos | 1040 | Local Indrustries. |  | 12 Month
10.2 | 10mm Rebar | Kg | 56 | Brands for reference only: BSRM, KSRM, GPH or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
103 | Cement | Cft | 8 | Brands for reference only: Bashundhara Cement, Shah Cement, Crown Cement, Premier Cement, Fresh Cement or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
10.4 | Local Sand | Cft | 32 | Local Indrustries. |  | 12 Month
10.5 | Brick Chips | Cft | 32 | Local Indrustries. |  | 12 Month
Total For Construction Earthing Pit Items
NAME:
IN THE CAPACITY OF:
DULY AUTHORIZED TO SIGN BID FOR AND ON BEHALF OF:
DATE:
OFFICIAL STAMP:

## Electrical Item for 4ext Clinic
Lot 3 Electrical Bill of Quantities (BOQ) with Stocks Items For PHC 1st Phase at Camp-4 Ext, at Ukhiya Cox's Bazar.
Item | Description (All the item must be supplied and installed as per TOR) | Unit of Measure | Quantity | Brands for reference only | Remarks | Reuired Minimum Warrenty | Offered Warranty | Offered Brand Name | Specification Sheet/Brochure/Catalogue/Data sheet /Test certificate is submitted? (Bidder may submit one of the mentioned required document above) (Yes/No)
SECTION 1: Supply of Distribution Boards and Circuit breakers
1.1 | MDB
| Three Phase Metal Distribution Board iP66, high qaulity rust proof and electric insulation paint, 100% water tight seal, with gastgets, fitted with digital Voltmeter+ammeters+selector switch (ph-N&ph-ph), and three phase indicator light, plexi-glass screen over the busbars) All other accessories as per technical specification & drawings. Size: 30"x24"x8", Copper bar size : 13"x1.25"x5 mm (3 No's For 3 Phase) and 8"x1.25"x 5mm (2 Nos For Neutral and Earthing) Maintain All Colour Code With Heatshrink Tube and Busbar Each Hole Distance Min 1.5" Mounted on insulator at both ends. Capacity : 200-300A, Customize For : (Incoming - 1 TP MCCB, Outgoing- 1 TP MCCB and 2 SP MCB, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 100A, TP MCCB, 400V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 80 A TP MCCB, 400 V, 10 KA (Outgoing) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.2 | SMDB-1
| Three Phase Metal Distribution Board iP66, high qaulity rust proof and electric insulation paint, 100% water tight seal, with gastgets, fitted with digital Voltmeter+ammeters+selector switch (ph-N&ph-ph), and three phase indicator light, plexi-glass screen over the busbars) All other accessories as per technical specification & drawings. Size: 30"x24"x8", Copper bar size : 13"x1.25"x5 mm (3 No's For 3 Phase) and 8"x1.25"x 5mm (2 Nos For Neutral and Earthing) Maintain All Colour Code With Heatshrink Tube and Busbar Each Hole Distance Min 1.5" Mounted on insulator at both ends. Capacity : 200-300A, Customize For : (Incoming - 1 TP MCCB, Outgoing- 2 TP MCCB and 1 TP MCB, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 80A TP MCCB, 400 V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 32A TP MCCB, 400 V, 10 KA (Outgoing) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 20A TP MCB, 400 V, 10 KA (Outgoing) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.3 | SDB-1
| Three Phase 18 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 32A TP MCCB, 400 V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 20A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 11 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.4 | SDB-2
| Three Phase 16 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 20A TP MCB, 400 V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 7 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 4 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.5 | SDB-3
| Three Phase 18 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 32A TP MCCB, 400 V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 20 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 4 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 10 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.6 | Three Phase AC Combiner Box: Three Phase (R,Y,B) and N+PE (Neutrul and Protection Earthing) Busbar Arrangement. Box Size: 18"x14"x8" Copper Busbar Busbar Thickness 5mm and shall be of suitable dimensions so as to accommodate the circuit breakers and busbars with insulated shroud with sufficient spacing including internal connection cables in the board and other materials, shall have hinged type door locks, circuit directory shall be suitable for concealed /surface mounted type having PVC cable glands/grommets of appropriate sizes, shall have knockout for conduits entry & exist, a suitable size copper plate earthing block must be provided inside the box. Customized for One Incoming TP MCCB and TP MCB For REB/PDB Incoming Circuit Breaker | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
1.7 | 100 A TP MCCB, 400 V, 10 KA (REB/PDB Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
Total For Distribution Boards and Circuit breakers
SECTION 2: Supply of Cabling
2.1 | Single wire 1.5 sqmm RED Cu/PVC, (BYA) | Roll | 21 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.2 | Single wire 1.5 sqmm Black Cu/PVC, (BYA) | Roll | 16 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.3 | Single wire 2.5 sqmm RED Cu/PVC, (BYA) | Roll | 16 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.4 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 13 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.5 | Single wire 4 sqmm RED Cu/PVC, (BYA) | Roll | 10 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.6 | Single wire 4 sqmm Black Cu/PVC, (BYA) | Roll | 10 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.7 | Single wire 4 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 10 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.8 | Single wire 6 sqmm RED Cu/PVC, (BYA) | Roll | 2 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.9 | Single wire 6 sqmm Black Cu/PVC, (BYA) | Roll | 1 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.10 | Single wire 6 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 1 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.11 | 1-4Cx16sqmm NYY | Meter | 60 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.12 | 1x16sqmm ECC Cu/PVC, (BYA) | Meter | 100 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.13 | 4-1Cx25sqmm NYY | Meter | 120 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.14 | 1-1Cx25sqmm ECC Cu/PVC, (BYA) | Meter | 50 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
Total For Cabling
SECTION 3: Supply of Piping & Conduits
3.1 | 1 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 700 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.2 | 1 inch PVC Joined Bend | Pcs | 36 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.3 | 1 inch PVC Joined Elbow | Pcs | 48 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.4 | 1 inch PVC Joined Socket | Pcs | 48 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.5 | 1 inch PVC Joined T Socket | Pcs | 48 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.6 | 1 inch PVC 2-Way Circular Box | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.7 | 1 inch PVC 3-Way Circular Box | Pcs | 24 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.8 | 1 inch PVC 4-Way Circular Box | Pcs | 48 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.9 | PVC Seal Joined Gum | Liter | 4 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.10 | 1.5 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 60 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.11 | 1.5 inch PVC Joined Socket | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.12 | 1.5 inch PVC Joined Bend | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.13 | 1.5 inch Joined Elbow | Pcs | 12 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.14 | PVC conduit 16x25 | Meter | 700 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.15 | PVC conduit 25x40 | Meter | 50 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.16 | PVC Flexible Pipe (Inside with steel)(Black) ; 0.5 Inch | Meter | 100 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | N/A
3.17 | PVC Flexible Pipe (Inside with steel)(Black) ; 1 Inch | Meter | 100 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | N/A
3.18 | PVC Flexible Pipe (Inside with steel)(Black) ; 1.5 Inch | Meter | 200 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | N/A
3.19 | Steel Saddle Clamp For Hose Pipe 0.5 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | N/A
3.20 | Steel Saddle Clamp For Hose Pipe 1 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | N/A
3.21 | Steel Saddle Clamp For Hose Pipe 1.5 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | N/A
Total For Piping & Conduits
SECTION 4: Supply of Lights, Sockets, and Light Switches
4.1 | Socket (universal type, multi-input, full set with back box) | Pcs | 85 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.2 | Socket (up to 20Amp)(three pin, for AC/Pump, full set with back box) | Pcs | 5 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.3 | LED Batten light full set (6500K, cool white color, minimum 100lm/w, 1.5meter max lenght) max 40 Watt | Pcs | 70 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.4 | LED light bulb (cool white color, E27 screw, min. 100lm/w )/ 12 Watt | Pcs | 24 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.5 | LED light bulb base (plastic, internal use, E27 screw, ) | Pcs | 24 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.6 | LED flood lights (heavy-duty structure, iP65, efficient heat dissipation, operating voltage (200 to 250 V), A+ energy saving, bright white light colour, minimum of 120Lm/W) ; 30 Watt | Pcs | 40 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.7 | Light Switches - one way, 1 Gang, min. 6 amp,(full set with back-box) | Pcs | 18 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.8 | Light Switches - one way, 2 Gang, min. 6 amp,(full set with back-box) | Pcs | 24 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.9 | Light Switches - one way, 3 Gang, min. 6 amp,(full set with back-box) | Pcs | 24 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
4.10 | Light Switches - one way, 4 Gang, min. 6 amp,(full set with back-box) | Pcs | 24 | Brands for reference only: Legrand, Schneider Electric, MK Electric, Panasonic, Walton, Energypac, Superstar, Pasha Energy, MEP, ABB, Philips/Signify, Osram/LEDVANCE, GE Lighting, Syska, Havells, and Sunplus. or Equivalent Brand. |  | 12 Month
Total For Sockets and Light
SECTION 5: Supply of Fans
5.1 | Ceiling Mounted Fan (Open Type, 56 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 41 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.2 | Ceiling Mounted Fan (Open Type, 36 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 2 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.3 | Wall mount fan (18 inch rotational, heavy duty, all Plastic, up to 40 inch diameter, full set, equipped with speed controler and On/Off switch | Pcs | 15 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.4 | Fans Speed Controller (rated up to 10 amp, full set with back box) | Pcs | 43 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.5 | Ventilation Fans (plastic type, mute, water proof configration); 12 Inch | Pcs | 6 | Brands for reference only: Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
Total For Fans
SECTION 6: Supply of Miscellaneous Items
6.1 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Red | Pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.2 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Yellow | pcs | 12 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.3 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Blue | pcs | 12 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.4 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Green | pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.5 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Black | pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.6 | Plastic rowel plug no.10 | Pcs | 4000 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.7 | 1 Inch twin thread cross-head wood screws suitable for plastic plug no.10 | Pcs | 4000 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.8 | PIB Tape (Black) | Pcs | 15 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.9 | Cable tie 200 mm | Pkt | 5 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.10 | Cable tie 300 mm | Pkt | 15 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | 12 Month
6.11 | S-shaped fan hooks made of 12mm rod, complete with fixing on angle by welding (including enamel painting on a corrosion resistive primer coat of red oxide) Size: As Per Site Measurment | Pcs | 43 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
6.12 | 2x2 inch Steel Angle Beam (L-shaped) for the ceiling fans installation on the roof beams, complete with weliding enamel painting on a corrosion resistive primer coat of red oxide. | Meter | 150 | BSRM, KSRM, and GPH., or Equivalent Brand. |  | 12 Month
6.13 | Buried Cable Warning Sign on 8”X8” Silver sheet with Plastic Paint | Nos | 4 | BSRM, KSRM, and GPH., or Equivalent Brand. |  | 12 Month
6.14 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6 rm RED | Pcs | 48 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.15 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Yellow | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.16 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Blue | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.17 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Black | Pcs | 48 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.18 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Green | Pcs | 48 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.19 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 16 rm | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.20 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 25 rm | Pcs | 36 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.21 | 10mm SS Royal Bolt | Nos | 18 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
6.22 | Silicone Gum | Nos | 5 | Sambond, V-tech and Oci , or Equivalent Brand. |  | 12 Month
6.23 | No. Tag (0-9); Every Digit | Packet | 1 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR/UN acceptance. |  | 12 Month
Total For Miscellaneous Items
SECTION 7: Supply of Earthing & Lightening Items
7.1 | 20 feet long, 40mm dia, 2.35 mm thickness GI Pipe, threaded both end (with 10mm thorough holes at every 500mm interval and every alternate hole 90 degree apart in direction) | Pcs | 8 | Brand for reference only: RFL Falcon, SIMEX, HATIM, GBTL, Steel Mark Ltd, or Equivalent Brand. |  | 12 Month
7.2 | Copper MGB ( 14" x3" x 1/4" ) with accessories | Pcs | 5 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.3 | Air terminals 2 feet long, 12.7mm dia, Copper. | Pcs | 13 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.4 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper | Pcs | 13 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.5 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper ( Joint Socket ) | Pcs | 12 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.6 | Copper solid strip 20mm x 3mm (60 mm2) | Meter | 150 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.7 | Ruppen Screw (2 inch) | Pcs | 150 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.8 | Copper Tape Clip | Pcs | 80 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.9 | Inspection box with copper busbar (30mm x 5mm x 200mm) with 18 gauge steel sheet | Pcs | 3 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.10 | Insulator for installation of MGB | pcs | 10 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.11 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 60 ft long | Pcs | 3 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.12 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 40 ft long | Pcs | 5 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.13 | U-shaped clamp (Copper, used for cable-cable connection): 50 sqmm, min 190 amp | Pcs | 16 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.14 | Rubber 5mm thickness 2' x 2' | Pcs | 5 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.15 | 25mm2 cable shoe/lug to connect 2SWG ECC | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
Total For Supply of Earthing & Lightening Items
SECTION 8: Supply and Installation of AC Item
8.1 | AC (Split type) Capacity: 18,000 BTU Energy Class : A++ Refrigerant: R410a Indoor Air Volume (m³/h): H-561/M-475/L-380 m³/h Inverter for Energy Saving Jet Cool & Heat Technology to drop temperature & heat up instantly Hidden LED display High density filter to remove more than 50% dust and other particles Cold-catalyst filter to remove formaldehyde and VOCs as harmful gases and odors Please Note: 1. The offer must include all necessary cables, ducts, pipes, and wires up to at least 15 feet to connect the indoor unit with the outdoor unit. The supplier should also provide a separate quote for each additional foot of cables, ducts, or pipes. 2. Equipment locations (indoor and outdoor units) must be agreed upon with a responsible person designated by UNHCR before installation. 3. The offer must include a robust, painted iron frame to hold and install the outdoor unit. Additionally, the supplier should provide a separate quote for a robust, painted iron security grill with a lock and key for the outdoor unit. 4.The power supply required for AC installation must be arranged independently by the vendors. 5. During the installation process of indoor and outdoor units, any drilling or screwing that causes damage to the structures must be repaired and restored to their original condition by the vendor. | Pcs | 2 | Gree AC, L.G. AC, Samsung AC, General AC or Equivalent Brand. |  | 12 Month
8.2 | AC (Split type) Capacity: 24,000 BTU Energy Class : A++ Refrigerant: R410a Indoor Air Volume (m³/h): H-561/M-475/L-380 m³/h Inverter for Energy Saving Jet Cool & Heat Technology to drop temperature & heat up instantly Hidden LED display High density filter to remove more than 50% dust and other particles Cold-catalyst filter to remove formaldehyde and VOCs as harmful gases and odors Please Note: 1. The offer must include all necessary cables, ducts, pipes, and wires up to at least 15 feet to connect the indoor unit with the outdoor unit. The supplier should also provide a separate quote for each additional foot of cables, ducts, or pipes. 2. Equipment locations (indoor and outdoor units) must be agreed upon with a responsible person designated by UNHCR before installation. 3. The offer must include a robust, painted iron frame to hold and install the outdoor unit. Additionally, the supplier should provide a separate quote for a robust, painted iron security grill with a lock and key for the outdoor unit. 4.The power supply required for AC installation must be arranged independently by the vendors. 5. During the installation process of indoor and outdoor units, any drilling or screwing that causes damage to the structures must be repaired and restored to their original condition by the vendor. | Pcs | 3 | Gree AC, L.G. AC, Samsung AC, General AC or Equivalent Brand. |  | 12 Month
Total For AC Items
SECTION 9: SECTION 9: Supply, Testing and Commissioning of Fire safety and Ditection Items
9.1 | Supply & fixing the following capacities multi purpose ABC dry chemical powder stored pressure type withmanometer system fire extinguisher suitable for repeated use complete with wall bracket, CO2 cartridge,easy refilling system etc. as per sample accepted & approved by the Engineer. Mono Amonium Phosphate based 40% ABC dry chemical agent & hasa moisture-proof, anti-caking properties. Working pressure : 12 BAR minimum & Test pressure : 25 BAR minimum. Proper fire rating (as per NFPA 10) according to the capacity of the extinguisher. Manufacturerer certificate shall have to be submitted if needed. Also sample of the dry chemical powder will be tested by the proper authority in Bangladesh if needed. Country of origin : CHINA / MALAYSIA or equivalent 5 Kg Capacity. | nos | 22 | Brand fpr reference only: Taifun, Sunrise, Hunter or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.2 | Supply & fixing the following capacities Carbon-di-Oxide type fire extinguisher suitable for repeated use complete with wall bracket, discharge nozzle etc. as per sample accepted & approved by the Engineer. Country of origin : CHINA / MALAYSIA or equivalent product. 5 Kg. capacity.. | nos | 12 | Brand fpr reference only: Taifun, Sunrise, Hunter or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.3 | Conventional fire alarm control panels : Supply and installation of 08 zone conventional fire alarm control panel with power supply unit, batteries and other accessories. The panel shall be complete with zone indicating LED, faultindication and optionaltelephone jack etc. The panel shall have input 220V AC and output 24V DC.Panel shall be confirmed UL listed / FM approvedapproved. Country of origin : AUSTRALIA / CANADA / JAPAN / USA / European countries or their licensed manufacturing units located globally. 08 zone capacity | Each | 1 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.4 | INITIATING DEVICES SMOKE DETECTOR ( CONVENTIONAL TYPE) Supply and installation of conventional smoke detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC. | Each | 23 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.5 | INITIATING DEVICES Heat Detector( CONVENTIONAL TYPE) Supply and installation of conventional heat detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC | Each | 7 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.6 | INITIATING DEVICES Manual call point ( CONVENTIONAL TYPE) Supply and installation of conventional type manual call point like break glass switch or single action pull station complete with back box and all other accessories and consumables. Power supply shall be 24V DC. It shall be UL listed / FM approved . | Each | 9 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.7 | Notification devices Strobe / horn with strobe Supply and installation of conventional type horn with strobe for notification purpose complete with back box, suitable to produce electronic sound level of 87 to 95 dBA @ 3 meter and illumination shall be not less than 75 candela red color shall be UL listed / FM approved . Power supply shall be 24VDC. | Each | 11 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.8 | SIGNALING CABLE WITH PVC CONDUIT & ACCESSORIES Surface conduit wiring with the following FPLR/ FPLP/ FPL type UL listed / FM Approved / LPCB Approved cable. PVC Insulation for each core shall be FR (Fire Rated) & Drain wire, shield (Aluminum Foil tape/ PET tape) shall meet the minimum requirement as per NEC (National Electric Code) or NFPA 70 or BS. Jacket shall be Fire Rated. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) . The work shall be carried out as per direction & approval of the Engineer in charge. 2C-1.5 sqmm (FPLR/ FPLP/ FPL ) cable with 1.5 sqmm (FR) ECC wire through PVC pipe of minimum inner dia 25 mm having wall thickness of 1.5 mm | Meter | 350 | Brand for reference only: Tianjie Indrustrial or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
Total for Supply, Testing and Commissioning of Fire safety and Ditection Items
SECTION 10: Supply of Construction Earthing Pit Items
10.1 | 1st Class Bricks | Nos | 1040 | Local Indrustries. |  | 12 Month
10.2 | 10mm Rebar | Kg | 56 | Brands for reference only: BSRM, KSRM, GPH or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
10.3 | Cement | Cft | 8 | Brands for reference only: Bashundhara Cement, Shah Cement, Crown Cement, Premier Cement, Fresh Cement or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
10.4 | Local Sand | Cft | 32 | Local Indrustries. |  | 12 Month
10.5 | Brick Chips | Cft | 32 | Local Indrustries. |  | 12 Month
Total For Construction Earthing Pit Items
NAME:
IN THE CAPACITY OF:
DULY AUTHORIZED TO SIGN BID FOR AND ON BEHALF OF:
DATE:
OFFICIAL STAMP:

## Electrical Item for Camp 26 NFI
Lot 4 Electrical Bill of Quantities (BOQ) with Stock Items For NFI Distribution Point at Camp 26, Nayapar, Teknaf.
Item | Description (All the item must be supplied and installed as per TOR) | Unit of Measure | Quantity | Brands for reference only | Remarks | Reuired Minimum Warrenty | Offered Warranty | Offered Brand Name | Specification Sheet/Brochure/Catalogue/Data sheet /Test certificate is submitted? (Bidder may submit one of the mentioned required document above) (Yes/No)
SECTION 1: Supply of Distribution Boards and Circuit breakers
1.1 | MDB
| Three Phase 16 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 20 A TP MCB, 400 V, 10 KA (Incoming) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A DP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.2 | SMDB
| Three Phase 16 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 20A, TP MCB, 400V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 20A, TP MCB, 400V, 10 KA (Outgoing) | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.3 | SDB-1 (Female Waiting Shade)
| Three Phase 14 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 20A, TP MCB, 400V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 220 V, 10 KA | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 220 V, 10 KA | Pcs | 6 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.4 | SDB-2 (Male Waiting Shade)
| Three Phase 14 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers based in Bangladesh, or equivalent, meeting the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
| 20A, TP MCB, 400V, 10 KA (Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 16 A SP MCB, 220 V, 10 KA | Pcs | 3 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
| 10 A SP MCB, 220 V, 10 KA | Pcs | 6 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
1.5 | Three Phase AC Combiner Box: Three Phase (R,Y,B) and N+PE (Neutrul and Protection Earthing) Busbar Arrangement. Box Size: 18"x14"x8" Copper Busbar Busbar Thickness 5mm and shall be of suitable dimensions so as to accommodate the circuit breakers and busbars with insulated shroud with sufficient spacing including internal connection cables in the board and other materials, shall have hinged type door locks, circuit directory shall be suitable for concealed /surface mounted type having PVC cable glands/grommets of appropriate sizes, shall have knockout for conduits entry & exist, a suitable size copper plate earthing block must be provided inside the box. Customized for One Incoming TP MCCB and TP MCB For REB/PDB Incoming Circuit Breaker | Pcs | 1 | Manufacturer for reference only: products manufactured by reputable manufacturers, or equivalent, fully compliant with the specified technical requirements and applicable standards, and subject to UNHCR acceptance. |  | 12 Month
1.6 | 20 A, TP MCB, 400V, 10 KA (REB/PDB Incoming) | Pcs | 1 | Schneider Electric, ABB, Siemens, Legrand, Havells, Chint, LS Electric, Hager, Eaton, Fuji Electric (for reference only) or equivalent products meeting or exceeding the required performance and quality standards, subject to UNHCR’s technical acceptance. |  | 12 Month
Total For Distribution Boards and Circuit breakers
SECTION 2: Supply of Cabling
2.1 | Single wire 1.5 sqmm RED Cu/PVC, (BYA) | Roll | 16 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.2 | Single wire 1.5 sqmm Black Cu/PVC, (BYA) | Roll | 12 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.3 | Single wire 2.5 sqmm RED Cu/PVC, (BYA) | Roll | 8 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.4 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 8 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.5 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 5 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.6 | Single wire 4 sqmm RED Cu/PVC, (BYA) | Roll | 6 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.7 | Single wire 4 sqmm Black Cu/PVC, (BYA) | Roll | 6 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.8 | Single wire 4 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 6 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.9 | 1x4C 6sqmm NYY | Meter | 100 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.10 | Single wire 6 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 1 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.11 | 1x4C 10sqmm NYY | Meter | 30 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.12 | 1x10sqmm ECC Cu/PVC, (BYA) | Meter | 30 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
2.13 | Earthing Cable Bare copper (solid copper ); For Main Earthing & LPS Purpose, Thickness- 12.7 mm | Meter | 80 | Brands for reference only: BRB Cable Industries, SQ Cables, Bizli Cables, BBS Cables, RR Imperial, Poly Cables, RR Kabel, Polycab, Prysmian Group, Ducab, Finolex, KEI Industries or equivalent, provided the offered products meet the requirements and applicable standards and are acceptable to UNHCR. |  | 12 Month
Total For Cabling
SECTION 3: Supply of Piping & Conduits
3.1 | 1 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 800 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.2 | 1 inch PVC Joined Bend | Pcs | 60 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.3 | 1 inch PVC Joined Socket | Pcs | 72 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.4 | 1 inch PVC T-Joint | Pcs | 72 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.5 | 1 inch PVC Elbow | Pcs | 72 | Brands for reference only: RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.6 | 1 inch PVC 4-Way Circular Box | Pcs | 48 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.7 | 1 inch PVC 3-Way Circular Box | Pcs | 48 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.8 | 1 inch PVC 2-Way Circular Box | Pcs | 48 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.9 | PVC Seal Joined Gum | Liter | 4 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.10 | 1.5 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 100 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.11 | 1.5 inch PVC Joined Socket | Pcs | 24 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.12 | 1.5 inch PVC Joined Bend | Pcs | 24 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.13 | 1.5 inch Joined Elbow | Pcs | 24 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.14 | PVC conduit 16x25 | Meter | 600 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.15 | PVC conduit 25x40 | Meter | 50 | RFL, NPOLY (National Polymer), LIRA, A‑1, BRB (PVC lines), Bashundhara, AKIJ, Bangladesh‑made UPVC from various compliant local manufacturers, Finolex, and Partex Pipes. or Equivalent Brand. |  | N/A
3.16 | PVC Flexible Pipe (Inside with steel)(Black) ; 0.5 Inch | Meter | 200 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | N/A
3.17 | PVC Flexible Pipe (Inside with steel)(Black) ; 1 Inch | Meter | 100 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | N/A
3.18 | PVC Flexible Pipe (Inside with steel)(Black) ; 1.5 Inch | Meter | 100 | Brands for reference only: Panda, RFL, LIRA, A‑1, NPOLY (National Polymer), AKIJ, Bashundhara, Superflex, National Flexible Pipe or equivalent, provided the offered product meets the specified technical requirements, is suitable for electrical installations, and is acceptable to UNHCR |  | N/A
3.19 | Steel Saddle Clamp For Hose Pipe 0.5 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | N/A
3.20 | Steel Saddle Clamp For Hose Pipe 1 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | N/A
3.21 | Steel Saddle Clamp For Hose Pipe 1.5 inch | Pcs | 36 | Brands for reference only: LIRA, A1. RFL, NPOLY and BRB, locally fabricated steel products, or equivalent, provided the offered item meets the specified technical requirements and is acceptable to UNHCR |  | N/A
Total For Piping & Conduits
SECTION 4: Supply of Lights, Sockets, and Light Switches
4.1 | Socket (universal type, multi-input, full set with back box) | Pcs | 18 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
4.2 | Socket (up to 20Amp)(three pin, for AC/Pump, full set with back box) | Pcs | 1 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
4.3 | LED Batten light full set (3500-5000K, cool white color, minimum 100lm/w, 1.5meter max lenght) max 40 Watt | Pcs | 50 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
4.4 | LED light bulb (cool white color, E27 screw, min. 100lm/w )/ 12 Watt | Pcs | 13 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
4.5 | LED light bulb base (plastic, internal use, E27 screw, ) | Pcs | 13 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
4.6 | LED flood lights (heavy-duty structure, iP65, efficient heat dissipation, operating voltage (200 to 250 V), A+ energy saving, bright white light colour, minimum of 120Lm/W) ; 30 Watt | Pcs | 40 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
4.7 | Light Switches - one way, 1 Gang, min. 6 amp,(full set with back-box) | Pcs | 12 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
4.8 | Light Switches - one way, 2 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
4.9 | Light Switches - one way, 3 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
4.10 | Light Switches - one way, 4 Gang, min. 6 amp,(full set with back-box) | Pcs | 18 | Walton, Superstar, Energypac, MEP, Sunplus, Energy Super, Energy+, Pasha Energy, MK, GE and Legrand or Equivalent Brand. |  | 12 Month
Total For Sockets and Light
SECTION 5: Supply of Fans
5.1 | Ceiling Mounted Fan (Open Type, 56 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 31 | Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.2 | Ceiling-mount Fan (Caged Type, 18 inch heavy duty, all plastic, up to 32 inch diameter, full set, equipped with speed controler and On/Off switch) | Pcs | 2 | Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.3 | Wall Mountain Fan (rotational,heavy duty,all plastic,up to 40 inch diameter,full set,equipped with speed controler and On/Off switch) | Pcs | 1 | Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.4 | Fans Speed Controller (rated up to 10 amp, full set with back box) | Pcs | 33 | Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
5.5 | Ventilation Fans (plastic type, mute, water proof configration); 12 Inch | Pcs | 7 | Walton, Vision, Energypac, Jamuna, GFC, Mira, Hemel, Bajaj, Super Klass, and BRB Fans or Equivalent Brand. |  | 12 Month
Total For Fans
SECTION 6: Supply of Miscellaneous Items
6.1 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Red | Pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.2 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Yellow | pcs | 12 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.3 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Blue | pcs | 12 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.4 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Green | pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.5 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Black | pcs | 36 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.6 | Plastic rowel plug no.10 | Pcs | 3000 | Tesa, Osaka, Superstar and Deer or Equivalent Brand. |  | N/A
6.7 | 1 Inch twin thread cross-head wood screws suitable for plastic plug no.10 | Pcs | 3000 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.8 | PIB Tape (Black) | Pcs | 15 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.9 | Cable tie 200 mm | Pkt | 7 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.10 | Cable tie 300 mm | Pkt | 12 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.11 | S-shaped fan hooks made of 12mm rod, complete with fixing on angle by welding (including enamel painting on a corrosion resistive primer coat of red oxide) Size: As Per Site Measurment | Pcs | 25 | SRM, KSRM, and GPH., or Equivalent Brand. |  | N/A
6.12 | 2x2 inch Steel Angle Beam (L-shaped) for the ceiling fans installation on the roof beams, complete with weliding enamel painting on a corrosion resistive primer coat of red oxide. | Meter | 150 | SRM, KSRM, and GPH., or Equivalent Brand. |  | N/A
6.13 | Buried Cable Warning Sign on 8”X8” Silver sheet with Plastic Paint | Nos | 6 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.14 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6 rm RED | Pcs | 24 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.15 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Yellow | Pcs | 24 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.16 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Blue | Pcs | 12 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.17 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Black | Pcs | 12 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.18 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Green | Pcs | 24 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.19 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 10 rm | Pcs | 48 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.20 | 10mm SS Royal Bolt | Nos | 18 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
6.21 | Silicone Gum | Nos | 5 | Sambond, V-tech and Oci , or Equivalent Brand. |  | N/A
6.22 | No. Tag (0-9); Every Digit | Packet | 1 | Reputed Bangladeshi Indrustries.and China Brand. |  | N/A
Total For Miscellaneous Items
SECTION 7: Supply of Earthing & Lightening Items
7.1 | 20 feet long, 40mm dia, 2.35 mm thickness GI Pipe, threaded both end (with 10mm thorough holes at every 500mm interval and every alternate hole 90 degree apart in direction) | Pcs | 10 | Brand for reference only: RFL Falcon, SIMEX, HATIM, GBTL, Steel Mark Ltd, or Equivalent Brand. |  | 12 Month
7.2 | Copper MGB ( 14" x3" x 1/4" ) with accessories | Pcs | 5 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.3 | Air terminals 2 feet long, 12.7mm dia, Copper. | Pcs | 11 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.4 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper | Pcs | 11 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.5 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper ( Joint Socket ) | Pcs | 12 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.6 | Copper solid strip 20mm x 3mm (60 mm2) | Meter | 200 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.7 | Ruppen Screw (2 inch) | Pcs | 200 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.8 | Copper Tape Clip | Pcs | 200 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.9 | Inspection box with copper busbar (30mm x 5mm x 200mm) with 18 gauge steel sheet | Pcs | 5 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.10 | Insulator for installation of MGB | pcs | 10 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.11 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 60 ft long | Pcs | 3 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.12 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 40 ft long | Pcs | 7 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.13 | U-shaped clamp (Copper, used for cable-cable connection): 50 sqmm, min 190 amp | Pcs | 20 | Brand for reference only: Coppertecch Indrustries Limited and HRR., or Equivalent Brand. |  | 12 Month
7.14 | Rubber 5mm thickness 2' x 2' | Pcs | 4 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
7.15 | 35mm2 cable shoe/lug to connect 2SWG ECC | Pcs | 24 | Reputable Bangladesh‑ or China‑based manufacturer, or equivalent, subject to UNHCR acceptance. |  | 12 Month
Total For Supply of Earthing & Lightening Items
SECTION 8: Supply of Fire Items Work and fire Items
8.1 | Supply & fixing the following capacities multi purpose ABC dry chemical powder stored pressure type withmanometer system fire extinguisher suitable for repeated use complete with wall bracket, CO2 cartridge,easy refilling system etc. as per sample accepted & approved by the Engineer. Mono Amonium Phosphate based 40% ABC dry chemical agent & hasa moisture-proof, anti-caking properties. Working pressure : 12 BAR minimum & Test pressure : 25 BAR minimum. Proper fire rating (as per NFPA 10) according to the capacity of the extinguisher. Manufacturerer certificate shall have to be submitted if needed. Also sample of the dry chemical powder will be tested by the proper authority in Bangladesh if needed. Country of origin : CHINA / MALAYSIA or equivalent 5 Kg Capacity. | nos | 8 | Brand fpr reference only: Taifun, Sunrise, Hunter or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.2 | Supply & fixing the following capacities Carbon-di-Oxide type fire extinguisher suitable for repeated use complete with wall bracket, discharge nozzle etc. as per sample accepted & approved by the Engineer. Country of origin : CHINA / MALAYSIA or equivalent product. 5 Kg. capacity.. | nos | 8 | Brand fpr reference only: Taifun, Sunrise, Hunter or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.3 | Conventional fire alarm control panels : Supply and installation of 08 zone conventional fire alarm control panel with power supply unit, batteries and other accessories. The panel shall be complete with zone indicating LED, faultindication and optionaltelephone jack etc. The panel shall have input 220V AC and output 24V DC.Panel shall be confirmed UL listed / FM approvedapproved. Country of origin : AUSTRALIA / CANADA / JAPAN / USA / European countries or their licensed manufacturing units located globally. 08 zone capacity | Each | 1 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.4 | INITIATING DEVICES SMOKE DETECTOR ( CONVENTIONAL TYPE) Supply and installation of conventional smoke detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC. | Each | 4 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.5 | INITIATING DEVICES Manual call point ( CONVENTIONAL TYPE) Supply and installation of conventional type manual call point like break glass switch or single action pull station complete with back box and all other accessories and consumables. Power supply shall be 24V DC. It shall be UL listed / FM approved . | Each | 4 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.6 | Notification devices Strobe / horn with strobe Supply and installation of conventional type horn with strobe for notification purpose complete with back box, suitable to produce electronic sound level of 87 to 95 dBA @ 3 meter and illumination shall be not less than 75 candela red color shall be UL listed / FM approved . Power supply shall be 24VDC. | Each | 5 | Brand for reference only: Asenware, COOPER, Triga, Fiffco or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
8.7 | SIGNALING CABLE WITH PVC CONDUIT & ACCESSORIES Surface conduit wiring with the following FPLR/ FPLP/ FPL type UL listed / FM Approved / LPCB Approved cable. PVC Insulation for each core shall be FR (Fire Rated) & Drain wire, shield (Aluminum Foil tape/ PET tape) shall meet the minimum requirement as per NEC (National Electric Code) or NFPA 70 or BS. Jacket shall be Fire Rated. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) . The work shall be carried out as per direction & approval of the Engineer in charge. 2C-1.5 sqmm (FPLR/ FPLP/ FPL ) cable with 1.5 sqmm (FR) ECC wire through PVC pipe of minimum inner dia 25 mm having wall thickness of 1.5 mm | Meter | 165 | Brand for reference only: Tianjie Indrustrial or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
Total For Fire Safety Items
SECTION 9: Supply of Construction Earthing Pit Items
9.1 | 1st Class Bricks | Nos | 1300 | Local Indrustries. |  | 12 Month
9.2 | 10mm Rebar | Kg | 70 | Brands for reference only: BSRM, KSRM, GPH or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.3 | Cement | Cft | 7 | Brands for reference only: Bashundhara Cement, Shah Cement, Crown Cement, Premier Cement, Fresh Cement or Equivalent Brand, subject to UNHCR acceptance. |  | 12 Month
9.4 | Local Sand | Cft | 40 | Local Indrustries. |  | 12 Month
9.5 | Brick Chips | Cft | 40 | Local Indrustries. |  | 12 Month
Total For Construction Earthing Pit Items
NAME:
IN THE CAPACITY OF:
DULY AUTHORIZED TO SIGN BID FOR AND ON BEHALF OF:
DATE:
OFFICIAL STAMP: