## Electrical Item for NFI at C1E
Lot 1 Electrical Bill of Quantities (BOQ) with Stock Items For NFI Distribution Point at Camp 1E, Ukhiya, Cox’s Bazar.
Item | Description (All the item must be supplied and installed as per TOR) | Unit of Measure | Quantity | Unit Cost of item | Unit Cost of Installation | Total
SECTION 1: Supply of Distribution Boards and Circuit breakers
1.1 | MDB of Camp 1E NFI Distribution Center
| Three Phase Metal Distribution Board iP66, high qaulity rust proof and electric insulation paint, 100% water tight seal, with gastgets, fitted with digital Voltmeter+ammeters+selector switch (ph-N&ph-ph), and three phase indicator light, plexi-glass screen over the busbars) All other accessories as per technical specification & drawings. Size: 30"x24"x8", Copper bar size : 13"x1.25"x5 mm (3 No's For 3 Phase) and 8"x1.25"x 5mm (2 Nos For Neutral and Earthing) Maintain All Colour Code With Heatshrink Tube and Busbar Each Hole Distance Min 1.5" Mounted on insulator at both ends. Capacity : 200-300A Customize For : (Incoming - 1 TP MCCB, Outgoing- 5 DP MCB approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 32 A TP MCCB, 400 V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 32 A DP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 |  |  | 0
| 20 A DP MCB, 220 V, 10 KA (Outgoing) | Pcs | 3 |  |  | 0
1.2 | DB 1: (Guard Room, EPR Room, Generator Room, Breast Feeding Room) |  |  |  | Total | 0
| 12 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 |  |  | 0
| 20A, DP MCB, 220V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 16 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 3 |  |  | 0
| 10 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 3 |  |  | 0
1.3 | DB 2: Office Rooms |  |  |  | Total | 0
| 10 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 |  |  | 0
| 20A, DP MCB, 220V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 16 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 |  |  | 0
| 10 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 3 |  |  | 0
1.4 | DB 3 : Waiting shade 1 (Male & Female) |  |  |  | Total | 0
| 12 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 |  |  | 0
| 32 A, DP MCB, 220V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 16 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 4 |  |  | 0
| 10 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 4 |  |  | 0
1.5 | Three Phase AC Combiner Box: Three Phase (R,Y,B) and N+PE (Neutrul and Protection Earthing) Busbar Arrangement. Box Size: 18"x14"x8" Copper Busbar Busbar Thickness 5mm and shall be of suitable dimensions so as to accommodate the circuit breakers and busbars with insulated shroud with sufficient spacing including internal connection cables in the board and other materials, shall have hinged type door locks, circuit directory shall be suitable for concealed /surface mounted type having PVC cable glands/grommets of appropriate sizes, shall have knockout for conduits entry & exist, a suitable size copper plate earthing block must be provided inside the box. Customized for One Incoming TP MCCB and TP MCB For REB/PDB Incoming Circuit Breaker | Pcs | 1 |  |  | 0
1.6 | 32 A, TP MCCB, 400V, 10 KA for (REB/PDB Incoming Circuit Breaker) | Pcs | 1 |  |  | 0
Total For Distribution Boards and Circuit breakers |  |  |  |  | Total | 0
SECTION 2: Supply of Cabling
2.1 | Single wire 1.5 sqmm RED Cu/PVC, (BYA) | Roll | 13 |  |  | 0
2.2 | Single wire 1.5 sqmm Black Cu/PVC, (BYA) | Roll | 10 |  |  | 0
2.3 | Single wire 2.5 sqmm RED Cu/PVC, (BYA) | Roll | 4 |  |  | 0
2.4 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 4 |  |  | 0
2.5 | Single wire 4 sqmm RED Cu/PVC, (BYA) | Roll | 3 |  |  | 0
2.6 | Single wire 4 sqmm Black Cu/PVC, (BYA) | Roll | 3 |  |  | 0
2.7 | Single wire 4 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 4 |  |  | 0
2.8 | 1x2C-4sqmm NYY | Meter | 40 |  |  | 0
2.9 | 1x2C-6sqmm NYY | Meter | 65 |  |  | 0
2.10 | 1x4C-6sqmm NYY | Meter | 45 |  |  | 0
2.11 | Single wire 6 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 2 |  |  | 0
2.12 | Single wire 16 sqmm Green Earthing Cu/PVC, (BYA) | Meter | 50 |  |  | 0
Total For Cabling |  |  |  |  | Total | 0
SECTION 3: Supply of Piping & Conduits
3.1 | 1 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 600 |  |  | 0
3.2 | 1 inch PVC Joined Bend | Pcs | 48 |  |  | 0
3.3 | 1 inch PVC Joined Socket | Pcs | 72 |  |  | 0
3.4 | 1 inch PVC T-Joint | Pcs | 60 |  |  | 0
3.5 | 1 inch PVC Elbow | Pcs | 60 |  |  | 0
3.6 | 1 inch PVC 4-Way Circular Box | Pcs | 36 |  |  | 0
3.7 | 1 inch PVC 3-Way Circular Box | Pcs | 36 |  |  | 0
3.8 | 1 inch PVC 2-Way Circular Box | Pcs | 36 |  |  | 0
3.9 | PVC Seal Joined Gum | Liter | 3 |  |  | 0
3.10 | 1.5 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 50 |  |  | 0
3.11 | 1.5 inch PVC Joined Socket | Pcs | 12 |  |  | 0
3.12 | 1.5 inch PVC Joined Bend | Pcs | 12 |  |  | 0
3.13 | 1.5 inch Joined Elbow | Pcs | 12 |  |  | 0
3.14 | PVC conduit 16x25 | Meter | 500 |  |  | 0
3.15 | PVC conduit 25x40 | Meter | 50 |  |  | 0
3.16 | PVC Flexible Pipe (Inside with steel)(Black) ; 0.5 Inch | Meter | 100 |  |  | 0
3.17 | PVC Flexible Pipe (Inside with steel)(Black) ; 1 Inch | Meter | 100 |  |  | 0
3.18 | PVC Flexible Pipe (Inside with steel)(Black) ; 1.5 Inch | Meter | 200 |  |  | 0
3.19 | Steel Saddle Clamp For Hose Pipe 0.5 inch | Pcs | 36 |  |  | 0
3.20 | Steel Saddle Clamp For Hose Pipe 1 inch | Pcs | 24 |  |  | 0
3.21 | Steel Saddle Clamp For Hose Pipe 1.5 inch | Pcs | 24 |  |  | 0
Total For Piping & Conduits |  |  |  |  | Total | 0
SECTION 4: Supply of Lights, Sockets, and Light Switches
4.1 | Socket (universal type, multi-input, full set with back box) | Pcs | 19 |  |  | 0
4.2 | Socket (up to 20Amp)(three pin, for AC/Pump, full set with back box) | Pcs | 1 |  |  | 0
4.3 | LED Batten light full set (3500-5000K, cool white color, minimum 100lm/w, 1.5meter max lenght) max 40 Watt | Pcs | 41 |  |  | 0
4.4 | LED light bulb (cool white color, E27 screw, min. 100lm/w )/ 12 Watt | Pcs | 22 |  |  | 0
4.5 | LED light bulb base (plastic, internal use, E27 screw, ) | Pcs | 22 |  |  | 0
4.6 | LED flood lights (heavy-duty structure, iP65, efficient heat dissipation, operating voltage (200 to 250 V), A+ energy saving, bright white light colour, minimum of 120Lm/W) ; 30 Watt | Pcs | 17 |  |  | 0
4.7 | Light Switches - one way, 1 Gang, min. 6 amp,(full set with back-box) | Pcs | 8 |  |  | 0
4.8 | Light Switches - one way, 2 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 |  |  | 0
4.9 | Light Switches - one way, 3 Gang, min. 6 amp,(full set with back-box) | Pcs | 12 |  |  | 0
4.10 | Light Switches - one way, 4 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 |  |  | 0
Total For Sockets and Light |  |  |  |  | Total | 0
SECTION 5: Supply of Fans
5.1 | Ceiling Mounted Fan (Open Type, 56 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 23 |  |  | 0
5.2 | Ceiling Mounted Fan (Open Type, 36 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 2 |  |  | 0
5.3 | Wall-Mountain Fan (Caged Type, 18 inch heavy duty, all plastic, up to 32 inch diameter, full set, equipped with speed controler and On/Off switch) | Pcs | 2 |  |  | 0
5.4 | Fans Speed Controller (rated up to 10 amp, full set with back box) | Pcs | 25 |  |  | 0
5.5 | Ventilation Fans (plastic type, mute, water proof configration); 12 Inch | Pcs | 6 |  |  | 0
Total For Fans |  |  |  |  | Total | 0
SECTION 6: Supply of Miscellaneous Items
6.1 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Red | Pcs | 36 |  |  | 0
6.2 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Yellow | pcs | 12 |  |  | 0
6.3 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Blue | pcs | 12 |  |  | 0
6.4 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Green | pcs | 36 |  |  | 0
6.5 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Black | pcs | 36 |  |  | 0
6.6 | Plastic rowel plug no.10 | Pcs | 3000 |  |  | 0
6.7 | 1 Inch twin thread cross-head wood screws suitable for plastic plug no.10 | Pcs | 3000 |  |  | 0
6.8 | PIB Tape (Black) | Pcs | 15 |  |  | 0
6.9 | Cable tie 200 mm | Pkt | 5 |  |  | 0
6.10 | Cable tie 300 mm | Pkt | 12 |  |  | 0
6.11 | S-shaped fan hooks made of 12mm rod, complete with fixing on angle by welding (including enamel painting on a corrosion resistive primer coat of red oxide) Size: As Per Site Measurment | Pcs | 25 |  |  | 0
6.12 | 2x2 inch Steel Angle Beam (L-shaped) for the ceiling fans installation on the roof beams, complete with weliding enamel painting on a corrosion resistive primer coat of red oxide. | Meter | 100 |  |  | 0
6.13 | Buried Cable Warning Sign on 8”X8” Silver sheet with Plastic Paint | Nos | 4 |  |  | 0
6.14 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6 rm RED | Pcs | 24 |  |  | 0
6.15 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Yellow | Pcs | 24 |  |  | 0
6.16 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Blue | Pcs | 12 |  |  | 0
6.17 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Black | Pcs | 12 |  |  | 0
6.18 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Green | Pcs | 24 |  |  | 0
6.19 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 10 rm | Pcs | 48 |  |  | 0
6.20 | 10mm SS Royal Bolt | Nos | 18 |  |  | 0
6.21 | Silicone Gum | Nos | 5 |  |  | 0
6.22 | No. Tag (0-9); Every Digit | Packet | 1 |  |  | 0
Total For Miscellaneous Items |  |  |  |  | Total | 0
SECTION 7: Supply of Earthing & Lightening Items
7.1 | 20 feet long, 40mm dia, 2.35 mm thickness GI Pipe, threaded both end (with 10mm thorough holes at every 500mm interval and every alternate hole 90 degree apart in direction) | Pcs | 9 |  |  | 0
7.2 | Copper MGB ( 14" x3" x 1/4" ) with accessories | Pcs | 4 |  |  | 0
7.3 | Air terminals 2 feet long, 12.7mm dia, Copper. | Pcs | 13 |  |  | 0
7.4 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper | Pcs | 13 |  |  | 0
7.5 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper ( Joint Socket ) | Pcs | 6 |  |  | 0
7.6 | Copper solid strip 20mm x 3mm (60 mm2) | Meter | 150 |  |  | 0
7.7 | Ruppen Screw (2 inch) | Pcs | 100 |  |  | 0
7.8 | Copper Tape Clip | Pcs | 100 |  |  | 0
7.9 | Inspection box with copper busbar (30mm x 5mm x 200mm) with 18 gauge steel sheet | Pcs | 5 |  |  | 0
7.10 | Insulator for installation of MGB | pcs | 8 |  |  | 0
7.11 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 60 ft long | Pcs | 3 |  |  | 0
7.12 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 40 ft long | Pcs | 6 |  |  | 0
7.13 | U-shaped clamp (Copper, used for cable-cable connection): 50 sqmm, min 190 amp | Pcs | 18 |  |  | 0
7.14 | Rubber 5mm thickness 2' x 2' | Pcs | 4 |  |  | 0
7.15 | 25mm2 cable shoe/lug to connect 2SWG ECC | Pcs | 24 |  |  | 0
Total For Supply of Earthing & Lightening Items |  |  |  |  | Total | 0
SECTION 8: Supply, Testing and Commissioning of Fire safety and Ditection Items
8.1 | Supply & fixing the following capacities multi purpose ABC dry chemical powder stored pressure type withmanometer system fire extinguisher suitable for repeated use complete with wall bracket, CO2 cartridge,easy refilling system etc. as per sample accepted & approved by the Engineer. Mono Amonium Phosphate based 40% ABC dry chemical agent & hasa moisture-proof, anti-caking properties. Working pressure : 12 BAR minimum & Test pressure : 25 BAR minimum. Proper fire rating (as per NFPA 10) according to the capacity of the extinguisher. Manufacturerer certificate shall have to be submitted if needed. Also sample of the dry chemical powder will be tested by the proper authority in Bangladesh if needed. Country of origin : CHINA / MALAYSIA or equivalent 5 Kg Capacity. | nos | 11 |  |  | 0
8.2 | Supply & fixing the following capacities Carbon-di-Oxide type fire extinguisher suitable for repeated use complete with wall bracket, discharge nozzle etc. as per sample accepted & approved by the Engineer. Country of origin : CHINA / MALAYSIA or equivalent product. 5 Kg. capacity.. | nos | 11 |  |  | 0
8.3 | Conventional fire alarm control panels : Supply and installation of 08 zone conventional fire alarm control panel with power supply unit, batteries and other accessories. The panel shall be complete with zone indicating LED, faultindication and optionaltelephone jack etc. The panel shall have input 220V AC and output 24V DC.Panel shall be confirmed UL listed / FM approvedapproved. Country of origin : AUSTRALIA / CANADA / JAPAN / USA / European countries or their licensed manufacturing units located globally. 08 zone capacity | Each | 1 |  |  | 0
8.4 | INITIATING DEVICES SMOKE DETECTOR ( CONVENTIONAL TYPE) Supply and installation of conventional smoke detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC. | Each | 4 |  |  | 0
8.5 | INITIATING DEVICES Heat Detector( CONVENTIONAL TYPE) Supply and installation of conventional heat detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC | Each | 1 |  |  | 0
8.6 | INITIATING DEVICES Manual call point ( CONVENTIONAL TYPE) Supply and installation of conventional type manual call point like break glass switch or single action pull station complete with back box and all other accessories and consumables. Power supply shall be 24V DC. It shall be UL listed / FM approved . | Each | 5 |  |  | 0
8.7 | Notification devices Strobe / horn with strobe Supply and installation of conventional type horn with strobe for notification purpose complete with back box, suitable to produce electronic sound level of 87 to 95 dBA @ 3 meter and illumination shall be not less than 75 candela red color shall be UL listed / FM approved . Power supply shall be 24VDC. | Each | 6 |  |  | 0
8.8 | SIGNALING CABLE WITH PVC CONDUIT & ACCESSORIES Surface conduit wiring with the following FPLR/ FPLP/ FPL type UL listed / FM Approved / LPCB Approved cable. PVC Insulation for each core shall be FR (Fire Rated) & Drain wire, shield (Aluminum Foil tape/ PET tape) shall meet the minimum requirement as per NEC (National Electric Code) or NFPA 70 or BS. Jacket shall be Fire Rated. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) . The work shall be carried out as per direction & approval of the Engineer in charge. 2C-1.5 sqmm (FPLR/ FPLP/ FPL ) cable with 1.5 sqmm (FR) ECC wire through PVC pipe of minimum inner dia 25 mm having wall thickness of 1.5 mm | Meter | 126 |  |  | 0
Total for Supply, Testing and Commissioning of Fire safety and Ditection Items |  |  |  |  | Total | 0
SECTION 9: Supply of Construction Earthing Pit Items |  |  |  | Unit cost of items
9.1 | 1st Class Bricks | Nos | 1170 |  |  | 0
9.2 | 10mm Rebar | Kg | 63 |  |  | 0
9.3 | Cement | Cft | 9 |  |  | 0
9.4 | Local Sand | Cft | 36 |  |  | 0
9.5 | Brick Chips | Cft | 36 |  |  | 0
Total of Supply of Construction of Earthing Pit Items |  |  |  | Total |  | 0
Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) |  |  |  | Unit cost of each boring
9.6 | Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | Job | 3 |  |  | 0
Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) |  |  |  | Unit cost of each boring
9.7 | Number of estimated earth pit required with 40 feet earth boring | Job | 6 |  |  | 0
Total Cost of Boring |  |  |  | Total |  | 0
Transportation and labor cost to move the items from the mentioned location in TOR to the sites |  |  |  | Cost of Transportation and Labor
9.7 | Items Mentioned in the Annex E to be moved to the sites | Job | 1 |  |  | 0
Total For Construction Earthing Pit Items
| SECTION 1: Supply of Distribution Boards and Circuit breakers | 0
| SECTION 2: Supply of Cabling | 0
| SECTION 3: Supply of Piping & Conduits | 0
| SECTION 4: Supply of Lights, Sockets, and Light Switches | 0
| SECTION 5: Supply of Fans | 0
| SECTION 6: Supply of Miscellaneous Items | 0
| SECTION 7: Supply of Earthing & Lightening Items | 0
| SECTION 8: Supply, Testing and Commissioning of Fire safety and Ditection Items | 0
| SECTION 9: Supply of Construction Earthing Pit Items | 0
| Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | 0
| Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) | 0
| Transportation and labor cost to move the items from the mentioned location in TOR to the sites | 0
| Grand Total | 0
VALIDITY OF OFFER:
NAME:
IN THE CAPACITY OF:
DULY AUTHORIZED TO SIGN BID FOR AND ON BEHALF OF:
DATE:
OFFICIAL STAMP:

## Electrical Item for Camp 4 PHC
Lot 2 Electrical Bill of Quantities (BOQ) with Stock Items For PHC Traning Center at Camp-4, Ukhiya, Cox's Bazar.
Item | Description (All the item must be supplied and installed as per TOR) | Unit of Measure | Quantity | Unit Cost of item | Unit Cost of Installation | Total
SECTION 1: Supply of Distribution Boards and Circuit breakers
1.1 | MDB
| Three Phase Metal Distribution Board iP66, high qaulity rust proof and electric insulation paint, 100% water tight seal, with gastgets, fitted with digital Voltmeter+ammeters+selector switch (ph-N&ph-ph), and three phase indicator light, plexi-glass screen over the busbars) All other accessories as per technical specification & drawings. Size: 30"x24"x8", Copper bar size : 13"x1.25"x5 mm (3 No's For 3 Phase) and 8"x1.25"x 5mm (2 Nos For Neutral and Earthing) Maintain All Colour Code With Heatshrink Tube and Busbar Each Hole Distance Min 1.5" Mounted on insulator at both ends. Capacity : 200-300A Customize For : (Incoming - 1 TP MCCB, Outgoing- 1 TP MCCB and 2 DP MCB and 1 SP MCB approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 40 A, TP MCCB, 400V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 32 A, TP MCCB, 400V, 10 KA (Outgoing) | Pcs | 1 |  |  | 0
| 32 A DP MCB, 230 V, 10 KA (Outgoing) | Pcs | 2 |  |  | 0
| 20 A DP MCB, 230 V, 10 KA (Outgoing) | Pcs | 2 |  |  | 0
| 16 A SP MCB, 230 V, 10 KA (Outgoing), | Pcs | 1 |  |  | 0
1.2 | SDB-1
| 12 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 |  |  | 0
| 32 A DP MCB, 220 V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 16 A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 4 |  |  | 0
| 10 A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 3 |  |  | 0
1.3 | SDB-2
| 10 Way; Plastic Distribution Board with Single Phase MCB Bar (For Internal Use, Surface Mount, High Quality Plastic, Complete Set with Din Rail Sealing Gasket, Neutral, Earth Wire Connector Strip) | Pcs | 1 |  |  | 0
| 20 A DP MCB, 230 V, 6 KA (Incoming) | Pcs | 1 |  |  | 0
| 20 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 2 |  |  | 0
| 10 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 3 |  |  | 0
1.4 | SDB-3
| Three Phase 24 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 32 A, TP MCB, 400V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 20 A, SP MCB, 230V, 10 KA (Outgoing) | Pcs | 3 |  |  | 0
| 16 A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 13 |  |  | 0
| 10 A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 5 |  |  | 0
1.5 | Three Phase AC Combiner Box: Three Phase (R,Y,B) and N+PE (Neutrul and Protection Earthing) Busbar Arrangement. Box Size: 18"x14"x8" Copper Busbar Busbar Thickness 5mm and shall be of suitable dimensions so as to accommodate the circuit breakers and busbars with insulated shroud with sufficient spacing including internal connection cables in the board and other materials, shall have hinged type door locks, circuit directory shall be suitable for concealed /surface mounted type having PVC cable glands/grommets of appropriate sizes, shall have knockout for conduits entry & exist, a suitable size copper plate earthing block must be provided inside the box. Customized for One Incoming TP MCCB and TP MCB For REB/PDB Incoming Circuit Breaker | Pcs | 1 |  |  | 0
1.6 | 40 A, TP MCCB, 400V, 10 KA (REB/PDB Incoming) | Pcs | 1 |  |  | 0
Total For Distribution Boards and Circuit breakers |  |  |  |  | Total | 0
SECTION 2: Supply of Cabling
2.1 | Single wire 1.5 sqmm RED Cu/PVC, (BYA) | Roll | 15 |  |  | 0
2.2 | Single wire 1.5 sqmm Black Cu/PVC, (BYA) | Roll | 13 |  |  | 0
2.3 | Single wire 2.5 sqmm RED Cu/PVC, (BYA) | Roll | 4 |  |  | 0
2.4 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 4 |  |  | 0
2.5 | Single wire 4 sqmm RED Cu/PVC, (BYA) | Roll | 5 |  |  | 0
2.6 | Single wire 4 sqmm Black Cu/PVC, (BYA) | Roll | 5 |  |  | 0
2.7 | Single wire 4 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 6 |  |  | 0
2.8 | 1x2C-4sqmm NYY | Meter | 40 |  |  | 0
2.9 | 1x2C-6sqmm NYY | Meter | 40 |  |  | 0
2.10 | 1x4C-6sqmm NYY | Meter | 60 |  |  | 0
2.11 | Single wire 6 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 1 |  |  | 0
2.12 | 1-4Cx10sqmm NYY | Meter | 50 |  |  | 0
2.13 | 1x10sqmm ECC Cu/PVC, (BYA) | Meter | 50 |  |  | 0
Total For Cabling |  |  |  |  | Total | 0
SECTION 3: Supply of Piping & Conduits
3.1 | 1 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 600 |  |  | 0
3.2 | 1 inch PVC Joined Bend | Pcs | 36 |  |  | 0
3.3 | 1 inch PVC Joined Elbow | Pcs | 36 |  |  | 0
3.4 | 1 inch PVC Joined Socket | Pcs | 36 |  |  | 0
3.5 | 1 inch PVC Joined T Socket | Pcs | 36 |  |  | 0
3.6 | 1 inch PVC 2-Way Circular Box | Pcs | 12 |  |  | 0
3.7 | 1 inch PVC 3-Way Circular Box | Pcs | 24 |  |  | 0
3.8 | 1 inch PVC 4-Way Circular Box | Pcs | 36 |  |  | 0
3.9 | PVC Seal Joined Gum | Liter | 3 |  |  | 0
3.10 | 1.5 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 40 |  |  | 0
3.11 | 1.5 inch PVC Joined Socket | Pcs | 12 |  |  | 0
3.12 | 1.5 inch PVC Joined Bend | Pcs | 12 |  |  | 0
3.13 | 1.5 inch Joined Elbow | Pcs | 12 |  |  | 0
3.14 | PVC conduit 16x25 | Meter | 600 |  |  | 0
3.15 | PVC conduit 25x40 | Meter | 50 |  |  | 0
3.16 | PVC Flexible Pipe (Inside with steel)(Black) ; 0.5 Inch | Meter | 100 |  |  | 0
3.17 | PVC Flexible Pipe (Inside with steel)(Black) ; 1 Inch | Meter | 100 |  |  | 0
3.18 | PVC Flexible Pipe (Inside with steel)(Black) ; 1.5 Inch | Meter | 100 |  |  | 0
3.19 | Steel Saddle Clamp For Hose Pipe 0.5 inch | Pcs | 36 |  |  | 0
3.20 | Steel Saddle Clamp For Hose Pipe 1 inch | Pcs | 36 |  |  | 0
3.21 | Steel Saddle Clamp For Hose Pipe 1.5 inch | Pcs | 36 |  |  | 0
Total For Piping & Conduits |  |  |  |  | Total | 0
SECTION 4: Supply of Lights, Sockets, and Light Switches
4.1 | Socket (universal type, multi-input, full set with back box) | Pcs | 58 |  |  | 0
4.2 | Socket (up to 20Amp)(three pin, for AC/Pump, full set with back box) | Pcs | 3 |  |  | 0
4.3 | LED Light square shape full set (2000-3000K, warm white color, minimum 100lm/w, 600mmx600mm max dimensions)' 40 Watt | Pcs | 22 |  |  | 0
4.4 | LED Batten light full set ( 6500K, cool white color, minimum 100lm/w, 1.5meter max lenght) max 40 Watt | Pcs | 22 |  |  | 0
4.5 | LED light bulb (cool white color, E27 screw, min. 100lm/w )/ 12 Watt | Pcs | 21 |  |  | 0
4.6 | LED light bulb base (plastic, internal use, E27 screw, ) | Pcs | 21 |  |  | 0
4.7 | LED flood lights (heavy-duty structure, iP65, efficient heat dissipation, operating voltage (200 to 250 V), A+ energy saving, bright white light colour, minimum of 120Lm/W) ; 30 Watt | Pcs | 7 |  |  | 0
4.8 | Light Switches - one way, 1 Gang, min. 6 amp,(full set with back-box) | Pcs | 12 |  |  | 0
4.9 | Light Switches - one way, 2 Gang, min. 6 amp,(full set with back-box) | Pcs | 16 |  |  | 0
4.10 | Light Switches - one way, 3 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 |  |  | 0
4.11 | Light Switches - one way, 4 Gang, min. 6 amp,(full set with back-box) | Pcs | 18 |  |  | 0
Total For Sockets and Light |  |  |  |  | Total | 0
SECTION 5: Supply of Fans
5.1 | Ceiling Mounted Fan (Open Type, 56 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 20 |  |  | 0
5.2 | Ceiling Mounted Fan (Open Type, 36 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 2 |  |  | 0
5.3 | Fans Speed Controller (rated up to 10 amp, full set with back box) | Pcs | 24 |  |  | 0
5.4 | Ventilation Fans (plastic type, mute, water proof configration); 12 Inch | Pcs | 14 |  |  | 0
Total For Fans |  |  |  |  | Total | 0
SECTION 6: Supply of Miscellaneous Items
6.1 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Red | Pcs | 36 |  |  | 0
6.2 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Yellow | pcs | 12 |  |  | 0
6.3 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Blue | pcs | 12 |  |  | 0
6.4 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Green | pcs | 36 |  |  | 0
6.5 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Black | pcs | 36 |  |  | 0
6.6 | Plastic rowel plug no.10 | Pcs | 3000 |  |  | 0
6.7 | 1 Inch twin thread cross-head wood screws suitable for plastic plug no.10 | Pcs | 3000 |  |  | 0
6.8 | PIB Tape (Black) | Pcs | 15 |  |  | 0
6.9 | Cable tie 200 mm | Pkt | 5 |  |  | 0
6.10 | Cable tie 300 mm | Pkt | 15 |  |  | 0
6.11 | S-shaped fan hooks made of 12mm rod, complete with fixing on angle by welding (including enamel painting on a corrosion resistive primer coat of red oxide) Size: As Per Site Measurment | Pcs | 22 |  |  | 0
6.12 | 2x2 inch Steel Angle Beam (L-shaped) for the ceiling fans installation on the roof beams, complete with weliding enamel painting on a corrosion resistive primer coat of red oxide. | Meter | 50 |  |  | 0
6.13 | Buried Cable Warning Sign on 8”X8” Silver sheet with Plastic Paint | Nos | 4 |  |  | 0
6.14 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6 rm RED | Pcs | 48 |  |  | 0
6.15 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Yellow | Pcs | 24 |  |  | 0
6.16 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Blue | Pcs | 24 |  |  | 0
6.17 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Black | Pcs | 48 |  |  | 0
6.18 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Green | Pcs | 48 |  |  | 0
6.19 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 16 rm | Pcs | 24 |  |  | 0
6.20 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 25 rm | Pcs | 36 |  |  | 0
6.21 | 10mm SS Royal Bolt | Nos | 18 |  |  | 0
6.22 | Silicone Gum | Nos | 5 |  |  | 0
6.23 | No. Tag (0-9); Every Digit | Packet | 1 |  |  | 0
Total For Miscellaneous Items |  |  |  |  | Total | 0
SECTION 7: Supply of Earthing & Lightening Items
7.1 | 20 feet long, 40mm dia, 2.35 mm thickness GI Pipe, threaded both end (with 10mm thorough holes at every 500mm interval and every alternate hole 90 degree apart in direction) | Pcs | 8 |  |  | 0
7.2 | Copper MGB ( 14" x3" x 1/4" ) with accessories | Pcs | 5 |  |  | 0
7.3 | Air terminals 2 feet long, 12.7mm dia, Copper. | Pcs | 9 |  |  | 0
7.4 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper | Pcs | 9 |  |  | 0
7.5 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper ( Joint Socket ) | Pcs | 5 |  |  | 0
7.6 | Copper solid strip 20mm x 3mm (60 mm2) | Meter | 70 |  |  | 0
7.7 | Ruppen Screw (2 inch) | Pcs | 100 |  |  | 0
7.8 | Copper Tape Clip | Pcs | 50 |  |  | 0
7.9 | Inspection box with copper busbar (30mm x 5mm x 200mm) with 18 gauge steel sheet | Pcs | 2 |  |  | 0
7.10 | Insulator for installation of MGB | pcs | 10 |  |  | 0
7.11 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 60 ft long | Pcs | 3 |  |  | 0
7.12 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 40 ft long | Pcs | 5 |  |  | 0
7.13 | U-shaped clamp (Copper, used for cable-cable connection): 50 sqmm, min 190 amp | Pcs | 16 |  |  | 0
7.14 | Rubber 5mm thickness 2' x 2' | Pcs | 5 |  |  | 0
7.15 | 25mm2 cable shoe/lug to connect 2SWG ECC | Pcs | 24 |  |  | 0
Total For Supply of Earthing & Lightening Items |  |  |  |  | Total | 0
SECTION 8: Supply and Installation of AC Item
8.1 | AC (Split type) Capacity: 24,000 BTU Energy Class : A++ Refrigerant: R410a Indoor Air Volume (m³/h): H-561/M-475/L-380 m³/h Inverter for Energy Saving Jet Cool & Heat Technology to drop temperature & heat up instantly Hidden LED display High density filter to remove more than 50% dust and other particles Cold-catalyst filter to remove formaldehyde and VOCs as harmful gases and odors Please Note: 1. The offer must include all necessary cables, ducts, pipes, and wires up to at least 15 feet to connect the indoor unit with the outdoor unit. The supplier should also provide a separate quote for each additional foot of cables, ducts, or pipes. 2. Equipment locations (indoor and outdoor units) must be agreed upon with a responsible person designated by UNHCR before installation. 3. The offer must include a robust, painted iron frame to hold and install the outdoor unit. Additionally, the supplier should provide a separate quote for a robust, painted iron security grill with a lock and key for the outdoor unit. 4.The power supply required for AC installation must be arranged independently by the vendors. 5. During the installation process of indoor and outdoor units, any drilling or screwing that causes damage to the structures must be repaired and restored to their original condition by the vendor. | Pcs | 2 |  |  | 0
Total For Supply of AC Items |  |  |  |  | Total | 0
SECTION 9: Supply, Testing and Commissioning of Fire safety and Ditection Items
9.1 | Supply & fixing the following capacities multi purpose ABC dry chemical powder stored pressure type withmanometer system fire extinguisher suitable for repeated use complete with wall bracket, CO2 cartridge,easy refilling system etc. as per sample accepted & approved by the Engineer. Mono Amonium Phosphate based 40% ABC dry chemical agent & hasa moisture-proof, anti-caking properties. Working pressure : 12 BAR minimum & Test pressure : 25 BAR minimum. Proper fire rating (as per NFPA 10) according to the capacity of the extinguisher. Manufacturerer certificate shall have to be submitted if needed. Also sample of the dry chemical powder will be tested by the proper authority in Bangladesh if needed. Country of origin : CHINA / MALAYSIA or equivalent 5 Kg Capacity. | nos | 11 |  |  | 0
9.2 | Supply & fixing the following capacities Carbon-di-Oxide type fire extinguisher suitable for repeated use complete with wall bracket, discharge nozzle etc. as per sample accepted & approved by the Engineer. Country of origin : CHINA / MALAYSIA or equivalent product. 5 Kg. capacity.. | nos | 11 |  |  | 0
9.3 | Conventional fire alarm control panels : Supply and installation of 08 zone conventional fire alarm control panel with power supply unit, batteries and other accessories. The panel shall be complete with zone indicating LED, faultindication and optionaltelephone jack etc. The panel shall have input 220V AC and output 24V DC.Panel shall be confirmed UL listed / FM approvedapproved. Country of origin : AUSTRALIA / CANADA / JAPAN / USA / European countries or their licensed manufacturing units located globally. 08 zone capacity | Each | 1 |  |  | 0
9.4 | INITIATING DEVICES SMOKE DETECTOR ( CONVENTIONAL TYPE) Supply and installation of conventional smoke detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC. | Each | 7 |  |  | 0
9.5 | INITIATING DEVICES Heat Detector( CONVENTIONAL TYPE) Supply and installation of conventional heat detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC | Each | 2 |  |  | 0
9.6 | INITIATING DEVICES Manual call point ( CONVENTIONAL TYPE) Supply and installation of conventional type manual call point like break glass switch or single action pull station complete with back box and all other accessories and consumables. Power supply shall be 24V DC. It shall be UL listed / FM approved . | Each | 11 |  |  | 0
9.7 | Notification devices Strobe / horn with strobe Supply and installation of conventional type horn with strobe for notification purpose complete with back box, suitable to produce electronic sound level of 87 to 95 dBA @ 3 meter and illumination shall be not less than 75 candela red color shall be UL listed / FM approved . Power supply shall be 24VDC. | Each | 13 |  |  | 0
9.8 | SIGNALING CABLE WITH PVC CONDUIT & ACCESSORIES Surface conduit wiring with the following FPLR/ FPLP/ FPL type UL listed / FM Approved / LPCB Approved cable. PVC Insulation for each core shall be FR (Fire Rated) & Drain wire, shield (Aluminum Foil tape/ PET tape) shall meet the minimum requirement as per NEC (National Electric Code) or NFPA 70 or BS. Jacket shall be Fire Rated. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) . The work shall be carried out as per direction & approval of the Engineer in charge. 2C-1.5 sqmm (FPLR/ FPLP/ FPL ) cable with 1.5 sqmm (FR) ECC wire through PVC pipe of minimum inner dia 25 mm having wall thickness of 1.5 mm | Meter | 209 |  |  | 0
Total for Supply, Testing and Commissioning of Fire safety and Ditection Items |  |  |  |  | Total | 0
SECTION 10: Supply of Construction Earthing Pit Items
10.1 | 1st Class Bricks | Nos | 1040 |  |  | 0
10.2 | 10mm Rebar | Kg | 56 |  |  | 0
103 | Cement | Cft | 8 |  |  | 0
10.4 | Local Sand | Cft | 32 |  |  | 0
10.5 | Brick Chips | Cft | 32 |  |  | 0
Total For Construction Earthing Pit Items |  |  |  |  | Total | 0
Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) |  |  |  | Unit cost of each boring construction
9.6 | Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | Job | 3 |  |  | 0
Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) |  |  |  | Unit cost of each boring construction
9.7 | Number of estimated earth pit required with 40 feet earth boring | Job | 5 |  |  | 0
Total Cost of Boring |  |  |  | Total |  | 0
Transportation and labor cost to move the items from the mentioned location in TOR to the sites |  |  |  | Cost of Transportation and Labor
9.7 | Items Mentioned in the Annex E to be moved to the sites | Job | 1 |  |  | 0
Total For Construction Earthing Pit Items
| SECTION 1: Supply of Distribution Boards and Circuit breakers | 0
| SECTION 2: Supply of Cabling | 0
| SECTION 3: Supply of Piping & Conduits | 0
| SECTION 4: Supply of Lights, Sockets, and Light Switches | 0
| SECTION 5: Supply of Fans | 0
| SECTION 6: Supply of Miscellaneous Items | 0
| SECTION 7: Supply of Earthing & Lightening Items | 0
| SECTION 8: Supply and Installation of AC Item | 0
| SECTION 9: SECTION 9: Supply, Testing and Commissioning of Fire safety and Ditection Items | 0
| SECTION 10: Supply of Construction Earthing Pit Items | 0
| Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | 0
| Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) | 0
| Transportation and labor cost to move the items from the mentioned location in TOR to the sites | 0
| Grand Total | 0
VALIDITY OF OFFER:
NAME:
IN THE CAPACITY OF:
DULY AUTHORIZED TO SIGN BID FOR AND ON BEHALF OF:
DATE:
OFFICIAL STAMP:

## Electrical Item for 4ext Clinic
Lot 3 Electrical Bill of Quantities (BOQ) with Stocks Items For PHC 1st Phase at Camp-4 Ext, at Ukhiya Cox's Bazar.
Item | Description (All the item must be supplied and installed as per TOR) | Unit of Measure | Quantity | Unit Cost of item | Unit Cost of Installation | Total
SECTION 1: Supply of Distribution Boards and Circuit breakers
1.1 | MDB
| Three Phase Metal Distribution Board iP66, high qaulity rust proof and electric insulation paint, 100% water tight seal, with gastgets, fitted with digital Voltmeter+ammeters+selector switch (ph-N&ph-ph), and three phase indicator light, plexi-glass screen over the busbars) All other accessories as per technical specification & drawings. Size: 30"x24"x8", Copper bar size : 13"x1.25"x5 mm (3 No's For 3 Phase) and 8"x1.25"x 5mm (2 Nos For Neutral and Earthing) Maintain All Colour Code With Heatshrink Tube and Busbar Each Hole Distance Min 1.5" Mounted on insulator at both ends. Capacity : 200-300A, Customize For : (Incoming - 1 TP MCCB, Outgoing- 1 TP MCCB and 2 SP MCB, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 100A, TP MCCB, 400V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 80 A TP MCCB, 400 V, 10 KA (Outgoing) | Pcs | 1 |  |  | 0
| 16 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 |  |  | 0
1.2 | SMDB-1
| Three Phase Metal Distribution Board iP66, high qaulity rust proof and electric insulation paint, 100% water tight seal, with gastgets, fitted with digital Voltmeter+ammeters+selector switch (ph-N&ph-ph), and three phase indicator light, plexi-glass screen over the busbars) All other accessories as per technical specification & drawings. Size: 30"x24"x8", Copper bar size : 13"x1.25"x5 mm (3 No's For 3 Phase) and 8"x1.25"x 5mm (2 Nos For Neutral and Earthing) Maintain All Colour Code With Heatshrink Tube and Busbar Each Hole Distance Min 1.5" Mounted on insulator at both ends. Capacity : 200-300A, Customize For : (Incoming - 1 TP MCCB, Outgoing- 2 TP MCCB and 1 TP MCB, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 80A TP MCCB, 400 V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 32A TP MCCB, 400 V, 10 KA (Outgoing) | Pcs | 2 |  |  | 0
| 20A TP MCB, 400 V, 10 KA (Outgoing) | Pcs | 1 |  |  | 0
1.3 | SDB-1
| Three Phase 18 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 32A TP MCCB, 400 V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 20A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 3 |  |  | 0
| 16A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 11 |  |  | 0
| 10A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 3 |  |  | 0
1.4 | SDB-2
| Three Phase 16 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 20A TP MCB, 400 V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 16A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 7 |  |  | 0
| 10A SP MCB, 230 V, 10 KA (Outgoing) | Pcs | 4 |  |  | 0
1.5 | SDB-3
| Three Phase 18 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 32A TP MCCB, 400 V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 20 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 4 |  |  | 0
| 16 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 10 |  |  | 0
| 10 A SP MCB, 230 V, 6 KA (Outgoing) | Pcs | 3 |  |  | 0
1.6 | Three Phase AC Combiner Box: Three Phase (R,Y,B) and N+PE (Neutrul and Protection Earthing) Busbar Arrangement. Box Size: 18"x14"x8" Copper Busbar Busbar Thickness 5mm and shall be of suitable dimensions so as to accommodate the circuit breakers and busbars with insulated shroud with sufficient spacing including internal connection cables in the board and other materials, shall have hinged type door locks, circuit directory shall be suitable for concealed /surface mounted type having PVC cable glands/grommets of appropriate sizes, shall have knockout for conduits entry & exist, a suitable size copper plate earthing block must be provided inside the box. Customized for One Incoming TP MCCB and TP MCB For REB/PDB Incoming Circuit Breaker | Pcs | 1 |  |  | 0
1.7 | 100 A TP MCCB, 400 V, 10 KA (REB/PDB Incoming) | Pcs | 1 |  |  | 0
Total For Distribution Boards and Circuit breakers |  |  |  |  | Total | 0
SECTION 2: Supply of Cabling
2.1 | Single wire 1.5 sqmm RED Cu/PVC, (BYA) | Roll | 21 |  |  | 0
2.2 | Single wire 1.5 sqmm Black Cu/PVC, (BYA) | Roll | 16 |  |  | 0
2.3 | Single wire 2.5 sqmm RED Cu/PVC, (BYA) | Roll | 16 |  |  | 0
2.4 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 13 |  |  | 0
2.5 | Single wire 4 sqmm RED Cu/PVC, (BYA) | Roll | 10 |  |  | 0
2.6 | Single wire 4 sqmm Black Cu/PVC, (BYA) | Roll | 10 |  |  | 0
2.7 | Single wire 4 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 10 |  |  | 0
2.8 | Single wire 6 sqmm RED Cu/PVC, (BYA) | Roll | 2 |  |  | 0
2.9 | Single wire 6 sqmm Black Cu/PVC, (BYA) | Roll | 1 |  |  | 0
2.10 | Single wire 6 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 1 |  |  | 0
2.11 | 1-4Cx16sqmm NYY | Meter | 60 |  |  | 0
2.12 | 1x16sqmm ECC Cu/PVC, (BYA) | Meter | 100 |  |  | 0
2.13 | 4-1Cx25sqmm NYY | Meter | 120 |  |  | 0
2.14 | 1-1Cx25sqmm ECC Cu/PVC, (BYA) | Meter | 50 |  |  | 0
Total For Cabling |  |  |  |  | Total | 0
SECTION 3: Supply of Piping & Conduits
3.1 | 1 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 700 |  |  | 0
3.2 | 1 inch PVC Joined Bend | Pcs | 36 |  |  | 0
3.3 | 1 inch PVC Joined Elbow | Pcs | 48 |  |  | 0
3.4 | 1 inch PVC Joined Socket | Pcs | 48 |  |  | 0
3.5 | 1 inch PVC Joined T Socket | Pcs | 48 |  |  | 0
3.6 | 1 inch PVC 2-Way Circular Box | Pcs | 12 |  |  | 0
3.7 | 1 inch PVC 3-Way Circular Box | Pcs | 24 |  |  | 0
3.8 | 1 inch PVC 4-Way Circular Box | Pcs | 48 |  |  | 0
3.9 | PVC Seal Joined Gum | Liter | 4 |  |  | 0
3.10 | 1.5 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 60 |  |  | 0
3.11 | 1.5 inch PVC Joined Socket | Pcs | 12 |  |  | 0
3.12 | 1.5 inch PVC Joined Bend | Pcs | 12 |  |  | 0
3.13 | 1.5 inch Joined Elbow | Pcs | 12 |  |  | 0
3.14 | PVC conduit 16x25 | Meter | 700 |  |  | 0
3.15 | PVC conduit 25x40 | Meter | 50 |  |  | 0
3.16 | PVC Flexible Pipe (Inside with steel)(Black) ; 0.5 Inch | Meter | 100 |  |  | 0
3.17 | PVC Flexible Pipe (Inside with steel)(Black) ; 1 Inch | Meter | 100 |  |  | 0
3.18 | PVC Flexible Pipe (Inside with steel)(Black) ; 1.5 Inch | Meter | 200 |  |  | 0
3.19 | Steel Saddle Clamp For Hose Pipe 0.5 inch | Pcs | 36 |  |  | 0
3.20 | Steel Saddle Clamp For Hose Pipe 1 inch | Pcs | 36 |  |  | 0
3.21 | Steel Saddle Clamp For Hose Pipe 1.5 inch | Pcs | 36 |  |  | 0
Total For Piping & Conduits |  |  |  |  | Total | 0
SECTION 4: Supply of Lights, Sockets, and Light Switches
4.1 | Socket (universal type, multi-input, full set with back box) | Pcs | 85 |  |  | 0
4.2 | Socket (up to 20Amp)(three pin, for AC/Pump, full set with back box) | Pcs | 5 |  |  | 0
4.3 | LED Batten light full set (6500K, cool white color, minimum 100lm/w, 1.5meter max lenght) max 40 Watt | Pcs | 70 |  |  | 0
4.4 | LED light bulb (cool white color, E27 screw, min. 100lm/w )/ 12 Watt | Pcs | 24 |  |  | 0
4.5 | LED light bulb base (plastic, internal use, E27 screw, ) | Pcs | 24 |  |  | 0
4.6 | LED flood lights (heavy-duty structure, iP65, efficient heat dissipation, operating voltage (200 to 250 V), A+ energy saving, bright white light colour, minimum of 120Lm/W) ; 30 Watt | Pcs | 40 |  |  | 0
4.7 | Light Switches - one way, 1 Gang, min. 6 amp,(full set with back-box) | Pcs | 18 |  |  | 0
4.8 | Light Switches - one way, 2 Gang, min. 6 amp,(full set with back-box) | Pcs | 24 |  |  | 0
4.9 | Light Switches - one way, 3 Gang, min. 6 amp,(full set with back-box) | Pcs | 24 |  |  | 0
4.10 | Light Switches - one way, 4 Gang, min. 6 amp,(full set with back-box) | Pcs | 24 |  |  | 0
Total For Sockets and Light |  |  |  |  | Total | 0
SECTION 5: Supply of Fans
5.1 | Ceiling Mounted Fan (Open Type, 56 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 41 |  |  | 0
5.2 | Ceiling Mounted Fan (Open Type, 36 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 2 |  |  | 0
5.3 | Wall mount fan (18 inch rotational, heavy duty, all Plastic, up to 40 inch diameter, full set, equipped with speed controler and On/Off switch | Pcs | 15 |  |  | 0
5.4 | Fans Speed Controller (rated up to 10 amp, full set with back box) | Pcs | 43 |  |  | 0
5.5 | Ventilation Fans (plastic type, mute, water proof configration); 12 Inch | Pcs | 6 |  |  | 0
Total For Fans |  |  |  |  | Total | 0
SECTION 6: Supply of Miscellaneous Items
6.1 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Red | Pcs | 36 |  |  | 0
6.2 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Yellow | pcs | 12 |  |  | 0
6.3 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Blue | pcs | 12 |  |  | 0
6.4 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Green | pcs | 36 |  |  | 0
6.5 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Black | pcs | 36 |  |  | 0
6.6 | Plastic rowel plug no.10 | Pcs | 4000 |  |  | 0
6.7 | 1 Inch twin thread cross-head wood screws suitable for plastic plug no.10 | Pcs | 4000 |  |  | 0
6.8 | PIB Tape (Black) | Pcs | 15 |  |  | 0
6.9 | Cable tie 200 mm | Pkt | 5 |  |  | 0
6.10 | Cable tie 300 mm | Pkt | 15 |  |  | 0
6.11 | S-shaped fan hooks made of 12mm rod, complete with fixing on angle by welding (including enamel painting on a corrosion resistive primer coat of red oxide) Size: As Per Site Measurment | Pcs | 43 |  |  | 0
6.12 | 2x2 inch Steel Angle Beam (L-shaped) for the ceiling fans installation on the roof beams, complete with weliding enamel painting on a corrosion resistive primer coat of red oxide. | Meter | 150 |  |  | 0
6.13 | Buried Cable Warning Sign on 8”X8” Silver sheet with Plastic Paint | Nos | 4 |  |  | 0
6.14 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6 rm RED | Pcs | 48 |  |  | 0
6.15 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Yellow | Pcs | 24 |  |  | 0
6.16 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Blue | Pcs | 24 |  |  | 0
6.17 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Black | Pcs | 48 |  |  | 0
6.18 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Green | Pcs | 48 |  |  | 0
6.19 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 16 rm | Pcs | 24 |  |  | 0
6.20 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 25 rm | Pcs | 36 |  |  | 0
6.21 | 10mm SS Royal Bolt | Nos | 18 |  |  | 0
6.22 | Silicone Gum | Nos | 5 |  |  | 0
6.23 | No. Tag (0-9); Every Digit | Packet | 1 |  |  | 0
Total For Miscellaneous Items |  |  |  |  | Total | 0
SECTION 7: Supply of Earthing & Lightening Items
7.1 | 20 feet long, 40mm dia, 2.35 mm thickness GI Pipe, threaded both end (with 10mm thorough holes at every 500mm interval and every alternate hole 90 degree apart in direction) | Pcs | 8 |  |  | 0
7.2 | Copper MGB ( 14" x3" x 1/4" ) with accessories | Pcs | 5 |  |  | 0
7.3 | Air terminals 2 feet long, 12.7mm dia, Copper. | Pcs | 13 |  |  | 0
7.4 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper | Pcs | 13 |  |  | 0
7.5 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper ( Joint Socket ) | Pcs | 12 |  |  | 0
7.6 | Copper solid strip 20mm x 3mm (60 mm2) | Meter | 150 |  |  | 0
7.7 | Ruppen Screw (2 inch) | Pcs | 150 |  |  | 0
7.8 | Copper Tape Clip | Pcs | 80 |  |  | 0
7.9 | Inspection box with copper busbar (30mm x 5mm x 200mm) with 18 gauge steel sheet | Pcs | 3 |  |  | 0
7.10 | Insulator for installation of MGB | pcs | 10 |  |  | 0
7.11 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 60 ft long | Pcs | 3 |  |  | 0
7.12 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 40 ft long | Pcs | 5 |  |  | 0
7.13 | U-shaped clamp (Copper, used for cable-cable connection): 50 sqmm, min 190 amp | Pcs | 16 |  |  | 0
7.14 | Rubber 5mm thickness 2' x 2' | Pcs | 5 |  |  | 0
7.15 | 25mm2 cable shoe/lug to connect 2SWG ECC | Pcs | 24 |  |  | 0
Total For Supply of Earthing & Lightening Items |  |  |  |  | Total | 0
SECTION 8: Supply and Installation of AC Item
8.1 | AC (Split type) Capacity: 18,000 BTU Energy Class : A++ Refrigerant: R410a Indoor Air Volume (m³/h): H-561/M-475/L-380 m³/h Inverter for Energy Saving Jet Cool & Heat Technology to drop temperature & heat up instantly Hidden LED display High density filter to remove more than 50% dust and other particles Cold-catalyst filter to remove formaldehyde and VOCs as harmful gases and odors Please Note: 1. The offer must include all necessary cables, ducts, pipes, and wires up to at least 15 feet to connect the indoor unit with the outdoor unit. The supplier should also provide a separate quote for each additional foot of cables, ducts, or pipes. 2. Equipment locations (indoor and outdoor units) must be agreed upon with a responsible person designated by UNHCR before installation. 3. The offer must include a robust, painted iron frame to hold and install the outdoor unit. Additionally, the supplier should provide a separate quote for a robust, painted iron security grill with a lock and key for the outdoor unit. 4.The power supply required for AC installation must be arranged independently by the vendors. 5. During the installation process of indoor and outdoor units, any drilling or screwing that causes damage to the structures must be repaired and restored to their original condition by the vendor. | Pcs | 2 |  |  | 0
8.2 | AC (Split type) Capacity: 24,000 BTU Energy Class : A++ Refrigerant: R410a Indoor Air Volume (m³/h): H-561/M-475/L-380 m³/h Inverter for Energy Saving Jet Cool & Heat Technology to drop temperature & heat up instantly Hidden LED display High density filter to remove more than 50% dust and other particles Cold-catalyst filter to remove formaldehyde and VOCs as harmful gases and odors Please Note: 1. The offer must include all necessary cables, ducts, pipes, and wires up to at least 15 feet to connect the indoor unit with the outdoor unit. The supplier should also provide a separate quote for each additional foot of cables, ducts, or pipes. 2. Equipment locations (indoor and outdoor units) must be agreed upon with a responsible person designated by UNHCR before installation. 3. The offer must include a robust, painted iron frame to hold and install the outdoor unit. Additionally, the supplier should provide a separate quote for a robust, painted iron security grill with a lock and key for the outdoor unit. 4.The power supply required for AC installation must be arranged independently by the vendors. 5. During the installation process of indoor and outdoor units, any drilling or screwing that causes damage to the structures must be repaired and restored to their original condition by the vendor. | Pcs | 3 |  |  | 0
Total For AC Items |  |  |  |  | Total | 0
SECTION 9: SECTION 9: Supply, Testing and Commissioning of Fire safety and Ditection Items
9.1 | Supply & fixing the following capacities multi purpose ABC dry chemical powder stored pressure type withmanometer system fire extinguisher suitable for repeated use complete with wall bracket, CO2 cartridge,easy refilling system etc. as per sample accepted & approved by the Engineer. Mono Amonium Phosphate based 40% ABC dry chemical agent & hasa moisture-proof, anti-caking properties. Working pressure : 12 BAR minimum & Test pressure : 25 BAR minimum. Proper fire rating (as per NFPA 10) according to the capacity of the extinguisher. Manufacturerer certificate shall have to be submitted if needed. Also sample of the dry chemical powder will be tested by the proper authority in Bangladesh if needed. Country of origin : CHINA / MALAYSIA or equivalent 5 Kg Capacity. | nos | 22 |  |  | 0
9.2 | Supply & fixing the following capacities Carbon-di-Oxide type fire extinguisher suitable for repeated use complete with wall bracket, discharge nozzle etc. as per sample accepted & approved by the Engineer. Country of origin : CHINA / MALAYSIA or equivalent product. 5 Kg. capacity.. | nos | 12 |  |  | 0
9.3 | Conventional fire alarm control panels : Supply and installation of 08 zone conventional fire alarm control panel with power supply unit, batteries and other accessories. The panel shall be complete with zone indicating LED, faultindication and optionaltelephone jack etc. The panel shall have input 220V AC and output 24V DC.Panel shall be confirmed UL listed / FM approvedapproved. Country of origin : AUSTRALIA / CANADA / JAPAN / USA / European countries or their licensed manufacturing units located globally. 08 zone capacity | Each | 1 |  |  | 0
9.4 | INITIATING DEVICES SMOKE DETECTOR ( CONVENTIONAL TYPE) Supply and installation of conventional smoke detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC. | Each | 23 |  |  | 0
9.5 | INITIATING DEVICES Heat Detector( CONVENTIONAL TYPE) Supply and installation of conventional heat detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC | Each | 7 |  |  | 0
9.6 | INITIATING DEVICES Manual call point ( CONVENTIONAL TYPE) Supply and installation of conventional type manual call point like break glass switch or single action pull station complete with back box and all other accessories and consumables. Power supply shall be 24V DC. It shall be UL listed / FM approved . | Each | 9 |  |  | 0
9.7 | Notification devices Strobe / horn with strobe Supply and installation of conventional type horn with strobe for notification purpose complete with back box, suitable to produce electronic sound level of 87 to 95 dBA @ 3 meter and illumination shall be not less than 75 candela red color shall be UL listed / FM approved . Power supply shall be 24VDC. | Each | 11 |  |  | 0
9.8 | SIGNALING CABLE WITH PVC CONDUIT & ACCESSORIES Surface conduit wiring with the following FPLR/ FPLP/ FPL type UL listed / FM Approved / LPCB Approved cable. PVC Insulation for each core shall be FR (Fire Rated) & Drain wire, shield (Aluminum Foil tape/ PET tape) shall meet the minimum requirement as per NEC (National Electric Code) or NFPA 70 or BS. Jacket shall be Fire Rated. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) . The work shall be carried out as per direction & approval of the Engineer in charge. 2C-1.5 sqmm (FPLR/ FPLP/ FPL ) cable with 1.5 sqmm (FR) ECC wire through PVC pipe of minimum inner dia 25 mm having wall thickness of 1.5 mm | Meter | 350 |  |  | 0
Total for Supply, Testing and Commissioning of Fire safety and Ditection Items |  |  |  |  | Total | 0
SECTION 10: Supply of Construction Earthing Pit Items
10.1 | 1st Class Bricks | Nos | 1040 |  |  | 0
10.2 | 10mm Rebar | Kg | 56 |  |  | 0
10.3 | Cement | Cft | 8 |  |  | 0
10.4 | Local Sand | Cft | 32 |  |  | 0
10.5 | Brick Chips | Cft | 32 |  |  | 0
Total For Construction Earthing Pit Items |  |  |  |  | Total | 0
Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) |  |  |  | Unit cost of each boring construction
9.6 | Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | Job | 3 |  |  | 0
Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) |  |  |  | Unit cost of each boring construction
9.7 | Number of estimated earth pit required with 40 feet earth boring | Job | 5 |  |  | 0
Total Cost of Boring |  |  |  | Total |  | 0
Transportation and labor cost to move the items from the mentioned location in TOR to the sites |  |  |  | Cost of Transportation and Labor
9.7 | Items Mentioned in the Annex E to be moved to the sites | Job | 1 |  |  | 0
Total For Construction Earthing Pit Items
| SECTION 1: Supply of Distribution Boards and Circuit breakers | 0
| SECTION 2: Supply of Cabling | 0
| SECTION 3: Supply of Piping & Conduits | 0
| SECTION 4: Supply of Lights, Sockets, and Light Switches | 0
| SECTION 5: Supply of Fans | 0
| SECTION 6: Supply of Miscellaneous Items | 0
| SECTION 7: Supply of Earthing & Lightening Items | 0
| SECTION 8: Supply and Installation of AC Item | 0
| SECTION 9: SECTION 9: Supply, Testing and Commissioning of Fire safety and Ditection Items | 0
| SECTION 10: Supply of Construction Earthing Pit Items | 0
| Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | 0
| Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) | 0
| Transportation and labor cost to move the items from the mentioned location in TOR to the sites | 0
| Grand Total | 0
VALIDITY OF OFFER:
NAME:
IN THE CAPACITY OF:
DULY AUTHORIZED TO SIGN BID FOR AND ON BEHALF OF:
DATE:
OFFICIAL STAMP:

## Electrical Item for Camp 26 NFI
Lot 4 Electrical Bill of Quantities (BOQ) with Stock Items For NFI Distribution Point at Camp 26, Nayapar, Teknaf.
Item | Description (All the item must be supplied and installed as per TOR) | Unit of Measure | Quantity | Unit Cost of item | Unit Cost of Installation | Total
SECTION 1: Supply of Distribution Boards and Circuit breakers
1.1 | MDB
| Three Phase 16 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 20 A TP MCB, 400 V, 10 KA (Incoming) | Pcs | 2 |  |  | 0
| 10 A DP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 |  |  | 0
| 10 A SP MCB, 220 V, 10 KA (Outgoing) | Pcs | 2 |  |  | 0
1.2 | SMDB
| Three Phase 16 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 20A, TP MCB, 400V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 20A, TP MCB, 400V, 10 KA (Outgoing) | Pcs | 3 |  |  | 0
1.3 | SDB-1 (Female Waiting Shade)
| Three Phase 14 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 20A, TP MCB, 400V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 16 A SP MCB, 220 V, 10 KA | Pcs | 3 |  |  | 0
| 10 A SP MCB, 220 V, 10 KA | Pcs | 6 |  |  | 0
1.4 | SDB-2 (Male Waiting Shade)
| Three Phase 14 Way; Metal Distribution Board , iP54, high qaulity rust proof and electric insulation paint, complete set with busbars for three phases, Neutral and Earth fitted. up to 200-300 amp, from reputed manufacturers like ABB/ SCHNEIDER/HAVELLS housing the following rated MCB/MCCB, all other accessories as per technical specification & drawings, approved by the Engineer-in-charge. | Pcs | 1 |  |  | 0
| 20A, TP MCB, 400V, 10 KA (Incoming) | Pcs | 1 |  |  | 0
| 16 A SP MCB, 220 V, 10 KA | Pcs | 3 |  |  | 0
| 10 A SP MCB, 220 V, 10 KA | Pcs | 6 |  |  | 0
1.5 | Three Phase AC Combiner Box: Three Phase (R,Y,B) and N+PE (Neutrul and Protection Earthing) Busbar Arrangement. Box Size: 18"x14"x8" Copper Busbar Busbar Thickness 5mm and shall be of suitable dimensions so as to accommodate the circuit breakers and busbars with insulated shroud with sufficient spacing including internal connection cables in the board and other materials, shall have hinged type door locks, circuit directory shall be suitable for concealed /surface mounted type having PVC cable glands/grommets of appropriate sizes, shall have knockout for conduits entry & exist, a suitable size copper plate earthing block must be provided inside the box. Customized for One Incoming TP MCCB and TP MCB For REB/PDB Incoming Circuit Breaker | Pcs | 1 |  |  | 0
1.6 | 20 A, TP MCB, 400V, 10 KA (REB/PDB Incoming) | Pcs | 1 |  |  | 0
Total For Distribution Boards and Circuit breakers |  |  |  |  | Total | 0
SECTION 2: Supply of Cabling
2.1 | Single wire 1.5 sqmm RED Cu/PVC, (BYA) | Roll | 16 |  |  | 0
2.2 | Single wire 1.5 sqmm Black Cu/PVC, (BYA) | Roll | 12 |  |  | 0
2.3 | Single wire 2.5 sqmm RED Cu/PVC, (BYA) | Roll | 8 |  |  | 0
2.4 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 8 |  |  | 0
2.5 | Single wire 2.5 sqmm Black Cu/PVC, (BYA) | Roll | 5 |  |  | 0
2.6 | Single wire 4 sqmm RED Cu/PVC, (BYA) | Roll | 6 |  |  | 0
2.7 | Single wire 4 sqmm Black Cu/PVC, (BYA) | Roll | 6 |  |  | 0
2.8 | Single wire 4 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 6 |  |  | 0
2.9 | 1x4C 6sqmm NYY | Meter | 100 |  |  | 0
2.10 | Single wire 6 sqmm Green Earthing Cu/PVC, (BYA) | Roll | 1 |  |  | 0
2.11 | 1x4C 10sqmm NYY | Meter | 30 |  |  | 0
2.12 | 1x10sqmm ECC Cu/PVC, (BYA) | Meter | 30 |  |  | 0
2.13 | Earthing Cable Bare copper (solid copper ); For Main Earthing & LPS Purpose, Thickness- 12.7 mm | Meter | 80 |  |  | 0
Total For Cabling |  |  |  |  | Total | 0
SECTION 3: Supply of Piping & Conduits
3.1 | 1 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 800 |  |  | 0
3.2 | 1 inch PVC Joined Bend | Pcs | 60 |  |  | 0
3.3 | 1 inch PVC Joined Socket | Pcs | 72 |  |  | 0
3.4 | 1 inch PVC T-Joint | Pcs | 72 |  |  | 0
3.5 | 1 inch PVC Elbow | Pcs | 72 |  |  | 0
3.6 | 1 inch PVC 4-Way Circular Box | Pcs | 48 |  |  | 0
3.7 | 1 inch PVC 3-Way Circular Box | Pcs | 48 |  |  | 0
3.8 | 1 inch PVC 2-Way Circular Box | Pcs | 48 |  |  | 0
3.9 | PVC Seal Joined Gum | Liter | 4 |  |  | 0
3.10 | 1.5 inch PVC Pipe (complete set with all necessary fitting, elbows, joints, glue and clamps) with T sockets. | Meter | 100 |  |  | 0
3.11 | 1.5 inch PVC Joined Socket | Pcs | 24 |  |  | 0
3.12 | 1.5 inch PVC Joined Bend | Pcs | 24 |  |  | 0
3.13 | 1.5 inch Joined Elbow | Pcs | 24 |  |  | 0
3.14 | PVC conduit 16x25 | Meter | 600 |  |  | 0
3.15 | PVC conduit 25x40 | Meter | 50 |  |  | 0
3.16 | PVC Flexible Pipe (Inside with steel)(Black) ; 0.5 Inch | Meter | 200 |  |  | 0
3.17 | PVC Flexible Pipe (Inside with steel)(Black) ; 1 Inch | Meter | 100 |  |  | 0
3.18 | PVC Flexible Pipe (Inside with steel)(Black) ; 1.5 Inch | Meter | 100 |  |  | 0
3.19 | Steel Saddle Clamp For Hose Pipe 0.5 inch | Pcs | 36 |  |  | 0
3.20 | Steel Saddle Clamp For Hose Pipe 1 inch | Pcs | 36 |  |  | 0
3.21 | Steel Saddle Clamp For Hose Pipe 1.5 inch | Pcs | 36 |  |  | 0
Total For Piping & Conduits |  |  |  |  | Total | 0
SECTION 4: Supply of Lights, Sockets, and Light Switches
4.1 | Socket (universal type, multi-input, full set with back box) | Pcs | 18 |  |  | 0
4.2 | Socket (up to 20Amp)(three pin, for AC/Pump, full set with back box) | Pcs | 1 |  |  | 0
4.3 | LED Batten light full set (3500-5000K, cool white color, minimum 100lm/w, 1.5meter max lenght) max 40 Watt | Pcs | 50 |  |  | 0
4.4 | LED light bulb (cool white color, E27 screw, min. 100lm/w )/ 12 Watt | Pcs | 13 |  |  | 0
4.5 | LED light bulb base (plastic, internal use, E27 screw, ) | Pcs | 13 |  |  | 0
4.6 | LED flood lights (heavy-duty structure, iP65, efficient heat dissipation, operating voltage (200 to 250 V), A+ energy saving, bright white light colour, minimum of 120Lm/W) ; 30 Watt | Pcs | 40 |  |  | 0
4.7 | Light Switches - one way, 1 Gang, min. 6 amp,(full set with back-box) | Pcs | 12 |  |  | 0
4.8 | Light Switches - one way, 2 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 |  |  | 0
4.9 | Light Switches - one way, 3 Gang, min. 6 amp,(full set with back-box) | Pcs | 14 |  |  | 0
4.10 | Light Switches - one way, 4 Gang, min. 6 amp,(full set with back-box) | Pcs | 18 |  |  | 0
Total For Sockets and Light |  |  |  |  | Total | 0
SECTION 5: Supply of Fans
5.1 | Ceiling Mounted Fan (Open Type, 56 inch, up to 100 W) full set with switch & speed controller including back-box. | Pcs | 31 |  |  | 0
5.2 | Ceiling-mount Fan (Caged Type, 18 inch heavy duty, all plastic, up to 32 inch diameter, full set, equipped with speed controler and On/Off switch) | Pcs | 2 |  |  | 0
5.3 | Wall Mountain Fan (rotational,heavy duty,all plastic,up to 40 inch diameter,full set,equipped with speed controler and On/Off switch) | Pcs | 1 |  |  | 0
5.4 | Fans Speed Controller (rated up to 10 amp, full set with back box) | Pcs | 33 |  |  | 0
5.5 | Ventilation Fans (plastic type, mute, water proof configration); 12 Inch | Pcs | 7 |  |  | 0
Total For Fans |  |  |  |  | Total | 0
SECTION 6: Supply of Miscellaneous Items
6.1 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Red | Pcs | 36 |  |  | 0
6.2 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Yellow | pcs | 12 |  |  | 0
6.3 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Blue | pcs | 12 |  |  | 0
6.4 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Green | pcs | 36 |  |  | 0
6.5 | PVC Electrical Insulation Tape (general purpose PVC insulating tape with high resistance to weather conditions and chemical reactions, minimum thickness of 0.18mm) All colors ; Black | pcs | 36 |  |  | 0
6.6 | Plastic rowel plug no.10 | Pcs | 3000 |  |  | 0
6.7 | 1 Inch twin thread cross-head wood screws suitable for plastic plug no.10 | Pcs | 3000 |  |  | 0
6.8 | PIB Tape (Black) | Pcs | 15 |  |  | 0
6.9 | Cable tie 200 mm | Pkt | 7 |  |  | 0
6.10 | Cable tie 300 mm | Pkt | 12 |  |  | 0
6.11 | S-shaped fan hooks made of 12mm rod, complete with fixing on angle by welding (including enamel painting on a corrosion resistive primer coat of red oxide) Size: As Per Site Measurment | Pcs | 25 |  |  | 0
6.12 | 2x2 inch Steel Angle Beam (L-shaped) for the ceiling fans installation on the roof beams, complete with weliding enamel painting on a corrosion resistive primer coat of red oxide. | Meter | 150 |  |  | 0
6.13 | Buried Cable Warning Sign on 8”X8” Silver sheet with Plastic Paint | Nos | 6 |  |  | 0
6.14 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6 rm RED | Pcs | 24 |  |  | 0
6.15 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Yellow | Pcs | 24 |  |  | 0
6.16 | Cabel lug/shoe (Pin-shaped tip and U-shaped tip) 6rm Blue | Pcs | 12 |  |  | 0
6.17 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Black | Pcs | 12 |  |  | 0
6.18 | Cabel lug/shoe (Pin-shaped tip and I-shaped tip) 6rm Green | Pcs | 24 |  |  | 0
6.19 | Cabel lug/shoe (O-shaped tip and U-shaped tip) 10 rm | Pcs | 48 |  |  | 0
6.20 | 10mm SS Royal Bolt | Nos | 18 |  |  | 0
6.21 | Silicone Gum | Nos | 5 |  |  | 0
6.22 | No. Tag (0-9); Every Digit | Packet | 1 |  |  | 0
Total For Miscellaneous Items |  |  |  |  | Total | 0
SECTION 7: Supply of Earthing & Lightening Items
7.1 | 20 feet long, 40mm dia, 2.35 mm thickness GI Pipe, threaded both end (with 10mm thorough holes at every 500mm interval and every alternate hole 90 degree apart in direction) | Pcs | 10 |  |  | 0
7.2 | Copper MGB ( 14" x3" x 1/4" ) with accessories | Pcs | 5 |  |  | 0
7.3 | Air terminals 2 feet long, 12.7mm dia, Copper. | Pcs | 11 |  |  | 0
7.4 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper | Pcs | 11 |  |  | 0
7.5 | Air terminals Base Plate 75x75x5mm with 4 holes on 4 sides and 4 sets of nut-bolts, all Copper ( Joint Socket ) | Pcs | 12 |  |  | 0
7.6 | Copper solid strip 20mm x 3mm (60 mm2) | Meter | 200 |  |  | 0
7.7 | Ruppen Screw (2 inch) | Pcs | 200 |  |  | 0
7.8 | Copper Tape Clip | Pcs | 200 |  |  | 0
7.9 | Inspection box with copper busbar (30mm x 5mm x 200mm) with 18 gauge steel sheet | Pcs | 5 |  |  | 0
7.10 | Insulator for installation of MGB | pcs | 10 |  |  | 0
7.11 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 60 ft long | Pcs | 3 |  |  | 0
7.12 | Solid Copper Earthing Rod 12.7mm dia. for main earthing - 40 ft long | Pcs | 7 |  |  | 0
7.13 | U-shaped clamp (Copper, used for cable-cable connection): 50 sqmm, min 190 amp | Pcs | 20 |  |  | 0
7.14 | Rubber 5mm thickness 2' x 2' | Pcs | 4 |  |  | 0
7.14 | 35mm2 cable shoe/lug to connect 2SWG ECC | Pcs | 24 |  |  | 0
Total For Supply of Earthing & Lightening Items |  |  |  |  | Total | 0
SECTION 8: Supply of Fire Items Work and fire Items
8.1 | Supply & fixing the following capacities multi purpose ABC dry chemical powder stored pressure type withmanometer system fire extinguisher suitable for repeated use complete with wall bracket, CO2 cartridge,easy refilling system etc. as per sample accepted & approved by the Engineer. Mono Amonium Phosphate based 40% ABC dry chemical agent & hasa moisture-proof, anti-caking properties. Working pressure : 12 BAR minimum & Test pressure : 25 BAR minimum. Proper fire rating (as per NFPA 10) according to the capacity of the extinguisher. Manufacturerer certificate shall have to be submitted if needed. Also sample of the dry chemical powder will be tested by the proper authority in Bangladesh if needed. Country of origin : CHINA / MALAYSIA or equivalent 5 Kg Capacity. | nos | 8 |  |  | 0
8.2 | Supply & fixing the following capacities Carbon-di-Oxide type fire extinguisher suitable for repeated use complete with wall bracket, discharge nozzle etc. as per sample accepted & approved by the Engineer. Country of origin : CHINA / MALAYSIA or equivalent product. 5 Kg. capacity.. | nos | 8 |  |  | 0
8.3 | Conventional fire alarm control panels : Supply and installation of 08 zone conventional fire alarm control panel with power supply unit, batteries and other accessories. The panel shall be complete with zone indicating LED, faultindication and optionaltelephone jack etc. The panel shall have input 220V AC and output 24V DC.Panel shall be confirmed UL listed / FM approvedapproved. Country of origin : AUSTRALIA / CANADA / JAPAN / USA / European countries or their licensed manufacturing units located globally. 08 zone capacity | Each | 1 |  |  | 0
8.4 | INITIATING DEVICES SMOKE DETECTOR ( CONVENTIONAL TYPE) Supply and installation of conventional smoke detector complete with base. Shall be UL listed / FM approved. Shall have built-in alarm LED. Power supply shall be 24VDC. | Each | 4 |  |  | 0
8.5 | INITIATING DEVICES Manual call point ( CONVENTIONAL TYPE) Supply and installation of conventional type manual call point like break glass switch or single action pull station complete with back box and all other accessories and consumables. Power supply shall be 24V DC. It shall be UL listed / FM approved . | Each | 4 |  |  | 0
8.6 | Notification devices Strobe / horn with strobe Supply and installation of conventional type horn with strobe for notification purpose complete with back box, suitable to produce electronic sound level of 87 to 95 dBA @ 3 meter and illumination shall be not less than 75 candela red color shall be UL listed / FM approved . Power supply shall be 24VDC. | Each | 5 |  |  | 0
8.7 | SIGNALING CABLE WITH PVC CONDUIT & ACCESSORIES Surface conduit wiring with the following FPLR/ FPLP/ FPL type UL listed / FM Approved / LPCB Approved cable. PVC Insulation for each core shall be FR (Fire Rated) & Drain wire, shield (Aluminum Foil tape/ PET tape) shall meet the minimum requirement as per NEC (National Electric Code) or NFPA 70 or BS. Jacket shall be Fire Rated. All electrical contacts shall be of brass / copper connected through connector or soldering (no twisting shall be allowed) . The work shall be carried out as per direction & approval of the Engineer in charge. 2C-1.5 sqmm (FPLR/ FPLP/ FPL ) cable with 1.5 sqmm (FR) ECC wire through PVC pipe of minimum inner dia 25 mm having wall thickness of 1.5 mm | Meter | 165 |  |  | 0
Total For Fire Safety Items |  |  |  |  | Total | 0
SECTION 9: Supply of Construction Earthing Pit Items
9.1 | 1st Class Bricks | Nos | 1300 |  |  | 0
9.2 | 10mm Rebar | Kg | 70 |  |  | 0
9.3 | Cement | Cft | 7 |  |  | 0
9.4 | Local Sand | Cft | 40 |  |  | 0
9.5 | Brick Chips | Cft | 40 |  |  | 0
Total For Construction Earthing Pit Items |  |  |  |  | Total | 0
Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) |  |  |  | Unit cost of each boring construction
9.6 | Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | Job | 3 |  |  | 0
Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) |  |  |  | Unit cost of each boring construction
9.7 | Number of estimated earth pit required with 40 feet earth boring | Job | 7 |  |  | 0
Total Cost of Boring |  |  |  | Total |  | 0
Transportation and labor cost to move the items from the mentioned location in TOR to the sites |  |  |  | Cost of Transportation and Labor
9.7 | Items Mentioned in the Annex E to be moved to the sites | Job | 1 |  |  | 0
Total For Construction Earthing Pit Items
| SECTION 1: Supply of Distribution Boards and Circuit breakers | 0
| SECTION 2: Supply of Cabling | 0
| SECTION 3: Supply of Piping & Conduits | 0
| SECTION 4: Supply of Lights, Sockets, and Light Switches | 0
| SECTION 5: Supply of Fans | 0
| SECTION 6: Supply of Miscellaneous Items | 0
| SECTION 7: Supply of Earthing & Lightening Items | 0
| SECTION 8: Supply of Fire Items Work and fire Items | 0
| SECTION 9: Supply of Construction Earthing Pit Items | 0
| Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | 0
| Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) | 0
| Transportation and labor cost to move the items from the mentioned location in TOR to the sites | 0
| Grand Total | 0
VALIDITY OF OFFER:
NAME:
IN THE CAPACITY OF:
DULY AUTHORIZED TO SIGN BID FOR AND ON BEHALF OF:
DATE:
OFFICIAL STAMP:

## Summary
Summary of Financial offer - Electrical Item Delivery and Installation Works at Four Site
Project Location/ Name | Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) | Total Electrical Item Delivery and Installation Cost as per the BOQ (in BDT) | Transportation and labor cost to move the items from the mentioned location in TOR to the sites | Total Cost (in BDT)
Lot 1 Camp 1E LPG/ NFI Depot | 0 | 0 | 0 | 0 | 0
Lot 2 Camp 4 training Facility | 0 | 0 | 0 | 0 | 0
Lot 3 Camp 4 Extension Health Facility | 0 | 0 | 0 | 0 | 0
Lot 4 LPG/ NFI Depot | 0 | 0 | 0 | 0 | 0

## Summary (2) (hidden)
Annex XX Financial offer form for Electrical Item Delivery and Installation Works at Four Site
Project Location/ Name | Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 60 feet earth boring (in BDT) | Each Earth Pit Construction Labor Cost (Earth Pit Size- 610mm×610mm×450mm) with 40 feet earth boring (in BDT) | Number of estimated earth pit required with 60 feet earth boring | Number of estimated earth pit required with 40 feet earth boring | Total Electrical Item Delivery and Installation Cost as per the BOQ (in BDT) | Transportation and labor cost to move the items from the mentioned location in TOR to the sites | Total Cost (in BDT)
Camp 4 Extension Health Facility | 0 | 0 | 3 | 5 | 0 | 0 | 8
Camp 4 training Facility | 0 | 0 | 3 | 5 | 0 | 0
Camp 1E LPG/ NFI Depot | 0 | 0 | 3 | 6 | 0 | 0
Camp 26 LPG/ NFI Depot | 0 | 0 | 3 | 7 | 0 | 0
Total Cost